## 18 September 2007

Mr. Will Tinkelenberg,								Corrected Copy

T.F.H. Architects,

100 Commercial Street,

Portland, Maine 04101

# RE: The Capacity to Handle Wastewater Flows, from the Proposed Renovation of a

# Multi-Family Residential Building, at 130 Eastern Promenade.

Dear Mr. Tinkelenberg:

The existing ten-inch diameter vitrified clay sewer pipe located in the Eastern Promenade has adequate capacity to transport, while The Portland Water District sewage treatment facility, located off Marginal Way, has adequate capacity to treat the total anticipated wastewater flows of 1,046 GPD, from the proposed residential renovation.

.

Anticipated Wastewater Flows from the Proposed Residential Rehabilitation Project:

4 Proposed One-Bedroom Units @ 180 GPD/Unit				=    720 GPD

5 Proposed Two-Bedroom Units @ 180 GPD/Unit				=    900 GPD

Less Existing Wastewater Flows of						=  (574 GPD)

Total Proposed Net Increase in Wastewater Flows for this Project 		= 1,046 GPD

The City combined sewer overflow (C.S.O.) abatement consent agreement (with the U.S.E.P.A., and with the Maine D.E.P.) requires C.S.O. abatement, as well as storm water mitigation, in order to offset any increase in sanitary flows, from all projects.

If the City can be of further assistance, please call 874-8832.

Sincerely,

CITY OF PORTLAND

Frank J Brancely, B.A., M.A.

Senior Engineering Technician

FJB

cc:	Alexander Q. Jaegerman, Director, Planning Division, Department of Planning, and Urban Development, City of Portland

Barbara Barhydt, Development Review Services Manager, Department of Planning, and Urban Development, City of Portland

David Margolis-Pineo, Deputy City Engineer, City of Portland

Michael Farmer, P.E., Project Engineer, City of Portland

Bradley A. Roland, P.E., Environmental Projects Engineer, City of Portland

Stephen K. Harris, Assistant Engineer, City of Portland

Jane Ward, Administrative Assistant, City of Portland

Desk file