## Sheet1
Code Summary | Urban Farm Fermentary
Project address: | 184 Anderson Street, Portland ME
Project type: | Existing space fit out for Assembly and Factory space
Square Foot | 10,885 sf +/- gross
Building code: | City of Portland IBC 2009
NFPA 101
Maine Human Rights Commission
IBC |  | CODE REF. | PAGE
Occupancy Type | MIXED USE: A-3 ASSEMBLY, F-2 FACTORY | 303.1, 306.3 | 23,24
General Building Height & Area Limits | Each portion of a bldg seperated by Fire Walls = separate bldg | 503.1 | 79
Allowable Stories, Area | (A-3) Stories: 1, Area: 6,000 (18,000 Sprinklered) | Table 503 | 80
| (F-1) Stories: 2, Area: 13,000 (39,000 Sprinklered) | Table 503 | 80
Allow Area Increase | (increase by 300% when sprinklered) | 506.3 | 82
Req'd Separation of Occupancies | A & F-2 - No Separation Required when Sprinklered | Table 508.3.3 | 86
Construction Type | Type VB Sprinklered | Table 601 | 89
Fire Walls | Fire Resistance Rating: Type V Assembly & F-2 = 2 Hour | Table 706.4 | 101
Fire Door Ratings | 2 Hour Wall = 1 1/2 Hour Door Assembly | Table 715.4 | 114
Occupant Load
BAY 1 & 2 | A-3: 3,391 SF / 15 = 226 | Table 1004.1.1 | 220
F-2: 1,715 SF / 100 = 18
Total Occupancy: 244
BAY 3 & 4 | F-2: 4,162 SF / 100 = 42
Total Occupancy: 42
Egress Width
BAY 1 & 2 | Staircase egress width: 244 / 2 * 0.3" = 36.6" | 1005.1 | 221
| Non-staircase egress width: 244 / 2 * 0.2" = 24.4" | 1005.1 | 221
BAY 3 & 4 | Staircase egress width: 42 / 2 * 0.3" = 6.3" | 1005.1 | 221
| Non-staircase egress width: 42 / 2 * 0.2" = 4.2" | 1005.1 | 221
Door Width | Minimum 32" Clear | 1008.1.1 | 224
Staircase Width | Minimum 44" (36" < 50 occupant load) | 1009.1 | 230
Common Path of Egress Travel | F Occupancy: 100'-0" maximum w/ sprinklers | 1014.3.1 | 238
Exit & Exit Access Doorways Req'd | 2 Exits: Assembly & Factory > 49 Occupant Load | Table 1015.1 | 239
Exit Doorway Arrangment | Separation shall be > 1/3 maximum diagonal distance | 1015.2.1.1 | 239
Exit Access Travel Distance | Occupancy A: 250'-0" max with sprinkler | Table 1016.1 | 240
| Occupancy F: 400'-0" max with sprinkler | Table 1016.1 | 240
Corridors | Fire Resistance Rating: Occupancy A & F sprinklered = 1 hour | Table 1018.1 | 241
| Not less than 44" min, 36" occupancy < 50 | 1018.2 | 242
Dead Ends | Maximum 20'-0" | 1018.4 | 242
| Occupancy F: 50'-0" when sprinklered | 1018.4.2 | 242
Assembly | Travel Distance: 250'-0" sprinklered | 1028.7 | 251
| Common Path of Egress Travel: 30'-0" | 1028.8 | 251
| Assembly Aisle widths: 42" when level with seating both sides | 1028.9.1.4 | 252
| Assembly Aisle widths: 36" when level with seating one side | 1028.9.1.5 | 252
NFPA |  | CODE REF. | PAGE
Occupancy Type | Assembly & Industrial | 6.1.2, 6.1.12 | 101-41
| Mixed Occupancies: Comply with most restrictive | 6.1.14.3.2 | 101-43
Means of Egress | Exit Access Corridors seperated with 1 Hour rating | 7.1.3 | 101-44
| Existing Stair dimensions | Table 7.2.2.2.1.1(b) | 101-55
Occupant Load | Assembly: Less Concentrated = 15 SF / person | Table 7.3.1.2 | 101-70
Industrial: 100 SF per person
BAY 1 & 2 | Assembly: 3,391 SF / 15 = 226 | T-7.3.1.2 | 101-70
Industrial: 1,715 SF / 100 = 18
Total Occupancy: 244
BAY 3 & 4 | Industrial: 4,162 SF / 100 = 42 | T-7.3.1.2 | 101-70
Total Occupancy: 42
Number of Exits | 2 min. | 7.4.1.1., 36.2.3.1 | 101-265
Egress Capacity: Level Components | 0.2" / person (244 / 2 x 0.2 = 24.4") | T-7.3.3.1 | 101-67
Egress Capacity: Stairs | 0.3" / person (244 / 2 x 0.3 = 36.6")
Min. Door Width | 32" | 7.2.1.2.4
Min. Corridor Width | 36" | 7.3.4.1
Construction & Compartmentalization | Separate buidlings, if a 2-hour or greater fire barrier wall | 8.2.1.3(1) | 101-80
Opening Protectives | 2-hour Fire barrier = 1 1/2 hour Door Assembly | Table 8.3.4.2 | 101-82
New Assembly Occupancies
Common Path of Travel | 20'-0", 75'-0" for < 50 occupants | 12.2.5.1.2 | 101-110
Dead End Corridors | 20'-0" max | 12.2.5.1.3 | 101-110
Travel Distance to Exits | 250'-0" if sprinkler throughout | 12.2.6.2 | 101-113
UPC (Uniform Plumbing Code) |  | CODE REF. | PAGE
Determine Occupancy Type: | "in accordance with the Building Code" | T4-1 Intro | 36
50% male, 50% female
IBC Occupancy | BAY 1 & 2:
Assembly: 226, Industrial: 18
Plumbing Fixture Count: | ASSEMBLY
| WC: Male 101-200 = 2 | T4-1 | 38
WC: Female 101-200 = 8
URINAL: 50 + 50 + 50 = 3
LAVATORY: 126 / 40 = 4 each
DRINKING FOUNTAIN: 151-400 = 2
INDUSTRIAL
WC: Male 1-10 = 1
WC: Female 1-10 = 1
LAVATORY: 1 per 10 = 2 total
DRINKING FOUNTAIN: 1 per 150 = 1
BAY 3 & 4:
Industrial: 42
INDUSTRIAL
WC: Male 11-25 = 2
WC: Female 11-25 = 2
LAVATORY: 1 per 10 = 5 total
DRINKING FOUNTAIN: 1 per 150 = 1
Exception to Occupant Load: | Where approved by the building official, the actual number of occupants for whom each occupied space, floor or building is designated, although less than those determined by calculation, shall be permitted to be used in the determination of the design occupant load. | IBC 1004.1.1 | IBC 220
T4-1(12) per building official
Design Occupant Load: | BAY 1 & 2: | By Architect/ Client
Employees: 6-8, estimated
Customers: 0-100 estimated
Plumbing Fixtures to be provided: | WC: Male 1-100: 1
WC: Female 1-50: 2
URINAL: 50 = 1
LAVATORY: 100 / 40 = 3 total
Design Occupant Load: | BAY 3 & 4: | By Architect/ Client
Employees: 1-5, estimated
Plumbing Fixtures to be provided: | WC: Male 1-10: 1
WC: Female 1-10: 1
LAVATORY: 1 / 10 = 2 total