# SECTION 15300 - NFPA-13R SPRINKLER SYSTEM

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS

General Provisions of Contract, including General and Supplementary conditions and General Requirements (if any) apply to work specified in this Section.

1.02	SCOPE

A.	It is the intent of this contract to provide automatic dry type sprinkler fire protection of PROP Phase III apartment buildings including all areas required to conform to NFPA -13R for Tenant spaces and NFPA 13 for Community Center space where applicable.  Provide freeze protected systems for all areas exposed to ambient air temperatures below 40F including garage under Cumberland Avenue South building.

B.	Contractor shall prepare hydraulic calculations of the fire protection systems in compliance with NFPA and I.S.O.

C.	Note that draft walls are installed in the attics.

1.03	RELATED WORK SPECIFIED ELSEWHERE

A.	Painting: Section 09900 - Painting.

B.	Electrical wiring: Division 16 sections.

1.04	CODE COMPLIANCE

A.	NFPA Compliance:  Install fire protection systems in accordance with NFPA -13R: "Standard for the Installation of Sprinkler Systems, 1999 Edition", NFPA 14: "Installation of Standpipe and Hose Systems, 1993 Edition", NFPA-13R:  "Installation of Sprinkler Systems in Residential Occupancies Up to and Including Four Stories in Height, 1999 Edition".

B.	UL Compliance:  Provide fire protection products in accordance with UL standards; provide UL label on each product.

C.	City of Portland, Maine and City of Westbrook, Maine Compliance:  Provide fire protection in accordance with City of Portland, Maine and City of Westbrook, Maine requirements and ordinances.

D.	Screw Thread Connections:  Comply with City of Portland and Westbrook Fire Department requirements for sizes, threading and arrangement of connections for fire department equipment to fire protection systems.

1.05	SUBMISSIONS

A.	Submittal:  Submit manufacturer's technical product data and installation instructions for fire protection materials and products.

B.	Approval Drawings:  Prepare approval drawings of fire protection systems indicating pipe sizes, pipe locations, fittings, shutoff and equipment.  Submit to Agency having jurisdiction for approval.  Submit one approved copy, bearing stamp and/or signature of Agency having jurisdiction, before proceeding with installation.

C.	Approval Calculations:  Prepare hydraulic calculations of fire protection systems.  Submit to Agency having jurisdiction for approval.  Submit one approved copy, bearing stamp and/or signature of Agency having jurisdiction, before proceeding with installation.

D.	Certificate of Installation:  Submit certificate upon completion of fire protection piping work which has been tested in accordance with NFPA- 13R and also that system is operational, complete, and has no defects.

E.	Maintenance Data:  Submit maintenance data and parts lists for fire protection materials and products.  Include this data, product data, shop drawings, approval drawings, approval calculations, certificate of installation, and record drawings in maintenance manual; in accordance with requirements of Division 1.

1.06	QUALITY ASSURANCE

A.	The entire fire protection automatic sprinkler system shall be designed, fabricated, installed and tested by a Contractor regularly engaged, a minimum of 5 years, in sprinkler installations of similar size and qualified to install sprinkler systems.  Sprinkler Contractor shall submit evidence of qualifications to the Architect under sprinkler firm's letterhead and signed by senior official of the corporation.

B.	In addition to complying with code compliance specified in Paragraph 1.3, conform to requirements of insurance underwriter, the 2000 International Fire Code and authority having local jurisdiction- City of Portland and City of Westbrook Fire Department, State Fire Marshall or both.

C.	Provide and coordinate location of access panels for sprinkler heads installed in areas with concealed heads.

D.	Provide adjustable, semi-recessed or two piece pipe escutcheons so that sprinkler head can be removed or repaired without damaging ceiling or ceiling tiles. Center sprinkler head in ceiling tile wherever possible.

E.	All sprinkler piping shall be run concealed.

F.	Coordinate location of exposed piping sprinkler heads with Architect.

# 1.07	WATER SUPPLY

A.	Water supply shall be from municipal water system.  Sprinkler Contractor shall test for available fire flow and pressure and report results in writing to Architect.  Coordinate tests with Portland Water District subsequent to PWD upgrade of water mains in street.

# 1.08	INSTALLATION

A.	All supervisory type valves and switches shall be automatic and interconnected to Fire Alarm Control Panel.

# PART 2 - PROTECTION

# 2.01	PIPING MATERIALS AND PRODUCTS

Provide piping materials and factory-fabricated piping products of sizes, types, pressure ratings, temperature ratings, and capacities as determined by Sprinkler Contractor to comply with installation requirements.  Provide sizes and types matching piping and equipment connections; provide fittings of materials which match pipe materials used in fire protection piping systems.  Where more than one type of materials or products are indicated, selection is Sprinkler Contractor's option.  All materials shall be in accordance with NFPA-13R requirements.

# 2.02	IDENTIFICATION

Provide identification in accordance with the following listing:

A.	Fire Protection Valves - Plastic valve tags.

B.	Fire Protection Signs - Provide the following signs.

# At each sprinkle valve, sign indicating what portion of system valve controls.

# At each outside alarm device, sign indicating what authority to call if device is activated.

C.	Install fire protection signs on piping in accordance with NFPA -13R requirements.

D.	Provide master schematic line diagram of sprinkler mains identifying pipe run and risers, major valves, test points, disconnect and shutoffs. Mount diagram on laminated plastic board and hang on wall near front door. Coordinate location with Architect.

# 2.3	PIPES AND PIPE FITTINGS

Provide pipes, and pipe fittings in accordance with the following listing:

A.	Black Steel Pipe - Schedule 40 for less than 8"; Schedule 30 for 8" and larger; Class 125, cast-iron threaded fittings and threaded joints, or mechanical grooved pipe couplings and fittings; cut-groove type.

B.	Black Steel Pipe - Schedule 10 for 5" and smaller; 0.134" wall thickness for 6"; and 0.188" walls thickness for 8" and 10"; wrought-steel; butt welding fittings and welded joints, or mechanical grooved pipe couplings and fittings; roll-groove or mechanical locking type.

C.	Comply with requirements of NFPA -13R for installation of fire protection piping materials.  Install piping products in accordance with manufacturer's written instructions, and in accordance with recognized industry practices to ensure that piping systems comply with requirements and serve its intended purposes.

D.	Coordinate with other work, including plumbing piping, as necessary to interface components of fire protection piping properly with other work.

E.	Install drain piping at low points of piping systems.  Provide dry drum drips where required.

F.	Install fire department connection valves in piping where required.

G.	Install paddle water flow indicators.

H.	Install manual shutoff at each audible alarm station.

I.	Install Inspector's test connection at most remote point from riser.

# 2.04	PIPING SPECIALTIES

Provide piping specialties in accordance with the following:

# Pipe escutcheons

Dielectric unions

Drip pans

Pipe sleeves

Sleeve seals

Fire Barrier Penetration Seals equal to SpecSeal Series 100 Sealant or equal by Hilti or 3-

# 2.05	SUPPORTS AND ANCHORS

Provide supports and anchors in accordance with the following listing:  Adjustable steel clevis hangers, adjustable steel band hangers, or adjustable band hangers, for horizontal-piping hangers and supports.  Two-bolt riser clamps for vertical piping supports.  Steel turnbuckles and malleable-iron sockets for hanger-rod attachments.  Concrete inserts, top-beam C-clamps, side beam or channel clamps or center beam clamps for building attachments.

# 2.06	VALVES

Provide valves in accordance with the following listing:

A.	Sectional Valves - Gate valves or butterfly valves; UL-listed.

B.	Check Valves - Swing check valves; UL-listed.

C.	Dry-Pipe Valves - Provide cast-iron dry-pipe valves, differential type, 175 PSI working pressure.

# OR

D.	Alarm Check Valve - Provide cast-iron water flow alarm check valve, 175 PSI working pressure.

E.	Fire Department Connection Valves - Provide flush type fire department connection iron swing check valve, 175 PSI rated working pressure and constructed of polish brass.

2.07	METERS AND GAGES

Provide meters and gages in accordance with the following listing:  Pressure gages, 0-250 PSI range.

2.08	FIRE PROTECTION SPECIALTIES

Provide fire protection specialties, UL-listed, in accordance with the following listing.  Provide sizes and types which mate and match piping and equipment connections.

A.	Water-Motor Gongs - Provide weatherproof, red enameled finish, water-motor gongs.

B.	Low Air Pressure Horn - Provide low air pressure horn as indicated.

C.	Air-Pressure Maintenance Device, Dry-Pipe System - Provide air-pressure maintenance device for dry-pipe standpipe piping as recommended by the manufacturer.

D.	Supervisory Switches - Provide products recommended by manufacturer for use in service indicated.

E.	Fire Protection Specialties Manufacturers - Allen (W.D.); Croker-Standard; Elkhart Brass; Grinnell Fire Protection Systems; Grunau Sprinkler; Guardian Fire Equipment; Potter Roemer; or Western Fire Equipment.

F.	Tamper switches for control valves.

G.	Install fire protection specialties as indicated and in accordance with NFPA- 13R.

Furnish wiring requirements to electrical installer for electrical wiring of supervisory switches.

2.09	AUTOMATIC SPRINKLERS

Provide automatic sprinklers in accordance with UL and FM listing.  Provide fusible links for 165F (74C) unless indicated otherwise.

Upright

Pendent

Vertical sidewall and Horizontal sidewall

Semi-recessed pendant

Flush dry-type pendent

Standard dry-type pendent and Standard dry-type upright

A.	Finish - White colored for occupied areas, cast brass for all other areas.

B.	Sprinkler Cabinet and Wrench - Furnish steel, baked red enamel, sprinkler box with capacity to store 12 sprinklers and wrench sized to sprinklers.

C.	Automatic Sprinklers Manufacturers - Automatic Sprinkler; Grinnell Fire Protection Systems; or Viking.

2.10	WALL TYPE SIAMESE CONNECTIONS

Provide wall flush type cast brass siamese connections and escutcheon plate assembly per City of Portland and Westbrook Fire Department requirements including fire department inlets with female hose connections, American National fire hose connection screw thread, equipped with individual drop clapper valves, equipped with plugs and chains, construction features as indicated, and constructed with the following additional construction features:

A.	Finish - Rough brass.

B.	Inlet Pipe - 4" pipe.

C.	Cast Lettering - "AUTO. SPKR.".

D.	Escutcheon - 12" diameter or 7" x 14" rectangular.

E.	Siamese Manufacturers - Croker-Standard; Elkhart Grass; or equal.

# PART 3 - EXECUTION

3.01	INSTALLATION

A.	Work shall be started as soon as the general construction permits.

B.	Risers are to be plumbed with adjacent construction.

C.	O.S. & Y. gate valves are to be aligned with adjacent walls or partitions to provide maximum clearance.

D.	Contractor shall be responsible for coordinating work with other trades.

3.02	SPRINKLER PIPING FLUSHING

Prior to connecting sprinkler risers for flushing, flush water feed mains, lead-in connections and control portions of sprinkler piping.  After fire sprinkler piping installation has been completed and before piping is placed in service, flush entire sprinkler system, as required to remove foreign substances, under pressure as specified in NFPA -13R.  Continue flushing until water is clear, and check to ensure that debris has not clogged sprinklers.

3.03	HYDROSTATIC TESTING

After flushing system, test fire sprinkler piping hydrostatically, for period of 2 hours, at not less than 200 PSI or at 50 PSI in excess of maximum static pressure when maximum static pressure is in excess of 150 PSI.  Check system for leakage of joints.  Measure hydrostatic pressure at low point of each system or zone being tested.

A.	Dry-Pipe Testing - Test dry-pipe hydrostatically except, in freezing conditions, test with air at pressures not less than 50 PSI, for a period of 2 hours.  Check system for leakage.  Leave differential dry-valve clappers open during test, to prevent damage.

B.	Repair or replace piping system as required to eliminate leakage in accordance with NFPA standards for "little or no leakage" and retest as specified to demonstrate compliance.

3.04	EXTRA EQUIPMENT

A.	Extra Heads - For each style and temperature range required, furnish additional sprinkler heads, amounting to one unit for every 100 installed units, but not less than 5 units of each.

B.	Extra Wrenches - Furnish 2 spanner wrenches for each type and size of valve connection and fire hose coupling.

C.	Cabinet - Emergency cabinet shall be a 12 capacity standard metal cabinet with head wrench and required spare heads.

3.05	QUALIFICATION

This contractor shall be well qualified by previous experience to complete this installation and may be required to submit evidence of such qualification to the engineers.

3.06	GUARANTEE

This contractor shall guarantee all materials and workmanship to be free from all defects for a period of one (1) year from date of final acceptance, and shall make good, repair or replace any defective work within that time at his own expense and with no cost to the owner.

# END OF SECTION 15300