# SECTION 07210 – BUILDING INSULATION

# PART I – GENERAL

  - RELATED DOCUMENTS

A.	Site drawings produced by Pinkham and Greer Consulting Engineers, foundation/basement plan drawings produced by TFH Architects PA and Structural Design Consulting, building drawings produced by TFH Architects, mechanical drawings produced by TFH Architects, electrical and lighting drawings produced by TFH Architects.  Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections apply to all sections.

  - SUMMARY

- This Section includes the following:

  - Concealed building insulation:

    - Fiberglass.

    - Rigid.

  - Vapor retarders.

- Related sections include the following:

  - Division 6 Section “Rough Carpentry” for foam-plastic board sheathing over wood framing.

  - Division 9 Section “Gypsum Board Assemblies” for installation in metal-framed assemblies of insulation specified by reference to this Section.

  - SUBMITTALS

- Product data:  For each type of product indicated.

- Samples for verification:  Full-size units for each type of exposed insulation indicated.

- Product test reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency, for insulation products.

- Research/evaluation reports:  For foam-plastic insulation.

  - QUALITY ASSURANCE

- Source limitations:  Obtain each type of building insulation through one source.

- Fire-test-response characteristics:  Provide insulation and related materials with the fire-test-response characteristics indicated, as determined by testing identical products per test method indicated below by UL or another testing and inspecting agency acceptable to authorities having jurisdiction.  Identify materials with appropriate markings of applicable testing and inspecting agency.

  - Surface-burning characteristics:  ASTM E 84.

  - Fire-resistance ratings:  ASTM E 119.

  - Combustion characteristics:  ASTM E 136.

  - DELIVERY, STORAGE AND HANDLING

- Protect insulation materials from physical damage and from deterioration by moisture, soiling and other sources.  Store inside and in a dry location.  Comply with manufacturer’s written instructions for handling, storing and protecting during installation.

# PART 2 -  PRODUCTS

  - MANUFACTURERS

- Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

  - Glass-fiber insulation:

    - CertainTeed Corporation.

    - Johns Manville Corporation.

    - Knauf Fiber Glass.

    - Owens Corning.

  - Rigid insulation:  Polyisocyanurate

    - Dow Corning

    - NRG

    - Celotex

  - Foil faced rigid insulation:  Polyisocyanurate

a.	Dow Corning

  - INSULATING MATERIALS

- General:  Provide insulating materials that comply with requirements and with referenced standards.

  - Pre-formed units:  Sizes to fit applications indicated; selected from manufacturer’s standard thickness, widths and lengths.

- Un-faced mineral-fiber blanket insulation:  ASTM C 665, Type 1 (blankets without membrane facing); consisting of fibers manufactured from glass; with maximum flame-spread and smoke-developed indices of 25 and 50, respectively; passing ASTM E 136 for combustion characteristics.

- Rigid insulation:  2” Polyisocyanurate foam sheets with a minimum of R-12.

- Foil faced rigid insulation:  2” Polyisocyanurate foam sheets with a minimum of R-13.

  - VAPOR RETARDERS

- Polyethylene vapor retarder:  ASTM D 4397, 6 mils (0.15 mm) thick, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

- Vapor-retarder tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.  Common duct tape will not be acceptable.

# PART 3 – EXECUTION

3.l	EXAMINATION

- Examine substrates and conditions, with Installer present, for compliance with requirements for Sections in which substrates and related work are specified and other conditions affecting performance.

- Proceed with installation only after unsatisfactory conditions have been corrected.

  - PREPARATION

- Clean substrates of substances harmful to insulation or vapor retarders, including removing projections capable of puncturing vapor retarders or of interfering with insulation attachment.

  - INSTALLATION, GENERAL

- Comply with insulation manufacturer’s written instructions applicable to products and application indicated.

- Install insulation that is undamaged, dry and unsoiled and that has not been left exposed at any time to ice and snow.

- Extend insulation in thickness indicated to envelop entire area to be insulated.  Cut and fit tightly around obstructions and fill voids with insulation.  Remove projections that interfere with placement.

- Water-piping coordination:  If water piping is located on inside of insulated exterior walls, coordinate location of piping to ensure that it is placed on warm side on insulation and insulation encapsulated piping.

- Apply single layer of insulation to produce thickness indicated, unless multiple layers are otherwise shown or required to make up total thickness.

  - INSTALLATION OF GENERAL BUILDING INSULATION

- Apply insulation units to substrates by method indicated, complying with manufacturer’s written instructions.  If no specific method is indicated, bond units to substrate with adhesive or use mechanical anchorage to provide permanent placement and support of units.

- Seal joints between closed-cell (non-breathing) insulation units by applying adhesive, mastic or sealant to edges of each unit to form a tight seal as units are shoved into place.  Fill voids in completed installation with adhesive, mastic or sealant as recommended by insulation manufacturer.

- Set vapor-retarder-faced units with vapor retarder to warm side of construction, unless otherwise indicated.  Do not obstruct ventilation spaces, except for fire stopping.

  - Tape joints and ruptures in vapor retarder and seal each continuous area of insulation to surrounding construction to ensure airtight installation.

- Install mineral-fiber blankets in cavities formed by roof framing members according to the following requirements:

  - Use blanket widths and lengths that fill the cavities formed by framing members.   If more than one length is required to fill cavity, provide lengths that will produce a snug fit between ends.

  - Place blankets in cavities formed by framing members to produce a friction fit between edges of insulation and adjoining framing members.

- Stuff glass-fiber, loose-fill insulation into miscellaneous voids and cavity spaces where shown.  Compact to approximately 40 percent of normal maximum volume equaling a density of approximately 2.5 lb/cu. Ft. (40 kg/cu. M).

F.	Install fiberglass insulation in basement ceiling prior to hanging GWB.

  - INSTALLATION OF VAPOR RETARDERS

- General:  Extend vapor retarder to extremities of areas to be protected from vapor transmission.  Secure in place with adhesives or other anchorage system as indicated.  Extend vapor retarder to cover miscellaneous voids in insulated substrates, including those filled with loose-fiber insulation.

- Seal vertical joints in vapor retarders over framing by lapping not less than two wall studs.  Fasten vapor retarders to framing at top, end and bottom edges; at perimeter of wall openings and at lap joints.  Space fasteners 16 inches (406 mm) o.c.

- Seal overlapping joints in vapor retarders with adhesives or vapor-retarder tape according to vapor-retarder manufacturer’s instructions.  Seal butt joints and fastener penetrations with vapor-retarder tape.  Locate all joints over framing members or other solid substrates.

- Firmly attach vapor retarders to substrates with mechanical fasteners or adhesives as recommended by vapor-retarder manufacturer.

  - PROTECTION

- Protect installed insulation and vapor retarders from damage due to harmful weather exposures, physical abuse and other causes.  Provide temporary coverings or enclosures where insulation is subject to abuse and cannot be concealed and protected by permanent construction immediately after installation.

# END OF SECTION 07210