From: 	Chris Pirone
To:	JF@portlandmaine.gov
Date: 	10/9/2013 11:00 AM
Subject: 	Munjoy heights

Fire comments

1. 20' access needs to be maintained in front of buildings. At end of road at isle it is showing 15'.
2. A template of our largest fire truck needs to be provided showing how the turnaround requirements per NFPA are being met since the road is more than 150'.
3. It appears an NFPA site code analysis has not completed. This needs to be done. Once completed it will indicate needs for amount and locations of fire hydrants.
4. A Professional Engineer with a discipline in Fire Protection will need to provide a stamped letter stating the site plan meets all applicable codes.
5. A Professional Engineer with a discipline in Fire Protection will need to provide a stamped letter stating that the building and fire protection final plans meets all applicable codes before submitting the plans for permit approval with the City.

Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410