| Business Name/Owner/Mgr/Location | Inspector | BENJAMIN WALLACE JR |  | Inspection Date |
| --- | --- | --- | --- | --- |
| 193 CONGRESS STREET |  |  |  | 8/24/2009 |  |
|  | Building Number | CBL | Inspection Type |  |
|  | 66505 |  | 013 M023001 | REINSPECTION |

- Building has a single means of egress.  One fire event will block all egress.

- Sprinkler system is incomplete, sprinkler heads are blocked, water supply is inadequate, and the system is not maintained.

- Fire alarm system is incomplete, there is no system smoke detection in the egress areas, and the sprinkler system is not supervised.

- Units and basement access are missing required one-hour fire door assemblies.

- The laundry room is not properly protected.

- There is no fire department knox box.

- Interior wall finish is not class A or B.