## Sheet1
SITE ADDRESS |  | 30 Merrill Street |  |  |  |  | DATE | 2017-05-20 |  | SLC # 1 | BSMT
|  | Portland | [8 empty] | 11 | PULL BY FACP
| FIRE ALARM TAKEOFF WORKSHEET | [9 empty] | 12 | WATER FLOW
TOTALS |  |  |  | BSMT | FIRST | SECOND | THIRD | FOURTH | ROOF |  | 13 | TAMPER
1 | FACP |  |  | 1 | [6 empty] | 14 | SMOKE FACP ROOM
1 | ANN |  |  |  | 1 | [5 empty] | 15 | HEAT TRASH ROOM
1 | DACT |  |  | 1 | [6 empty] | 16 | HEAT TRASH ROOM
1 | AES |  |  | 1 | [6 empty] | 17 | SMOKE HALL BSMT
9 | PD SMOKE |  |  | 5 | 2 | 1 | 1 |  |  |  | 18 | SMOKE HALL BSMT
2 | HD HEAT |  |  | 2 | [6 empty] | 19 | SMOKE HALL BSMT
11 | 6B BASE |  |  | 8 | 2 | 1 | 1 | 1 |  |  | 20 | SMOKE HALL BSMT
4 | PSDA DUAL ACTION PULL |  |  | 1 | 2 |  |  |  | 1 WP
|  |  |  | BSMT | FIRST | SECOND | THIRD | FOURTH | ROOF |  | 1ST FL
1 | STROBE | WALL MOUNT |  | 1 | [6 empty] | 21 | PULL REAR EXIT
9 | AUDIO/VISUAL CEILING MOUNT |  |  | 3 | 2 | 1 | 1 | 2 |  |  | 22 | SMOKE REAR HALL
7 | MINI-HORN WALL MOUNT APTS |  |  |  | 2 | 2 | 2 | 1 |  |  | 23 | SMOKE FRONT ENTRY
1 | WP HORN STROBE WALL MOUNT | [7 empty] | 1 WP |  | 24 | PULL FRONT ENTRY
|  |  |  | BSMT | FIRST | SECOND | THIRD | FOURTH
1 | MICRO INPUT MOD | [7 empty] | 1 |  | 2ND FL
1 | DIM DOUBLE INPUT MOD |  |  | 1 | [6 empty] | 25 | SMOKE STAIRWELL
1 | IM ISOLATOR MOD |  |  | 1 | [6 empty] | 3RD FL
1 | SPACE AGE SURGE 120VAC |  |  | 1 | [6 empty] | 25 | SMOKE STAIRWELL
4TH FL
Note | Roof top weather proof surface mount pull station has one micro input module that must be installed | [9 empty] | 26 | SMOKE STAIRWELL
| in a heated space. |  | ProPro will supply the weather proof pull station surface mount back box. | [7 empty] | ROOF
[11 empty] | 27 | PULL WATER PROOF SURFACE MOUNT
| Notification Appliance Circuits |  |  | APARTMENT MINI-HORNS WALL MOUNT
| NAC1 BSMT, 1ST, 2ND FLOOR |  |  | COMMON HALLWAY CEILING MOUNT
| NAC2 3RD-4TH-ROOF |  |  | BSMT STROBE WALL MOUNT
2ND FL
NAC 1 | BSMT | RED + OUT BLACK - OUT, YELLOW + RETURN GREEN - RETURN | [6 empty] | NAC 2 | AV
| STROBE | [8 empty] | AV | RED + OUT BLACK - OUT, YELLOW + RETURN GREEN - RETURN
| AV | [8 empty] | AV
| AV | [8 empty] | 3RD FL
| AV | [8 empty] | AV
| AV | RETURN NAC1 TO FACP ON YELLOW-GREEN TO TERMINAL STRIP | [7 empty] | AV | RETURN NAC2 TO FACP ON YELLOW-GREEN TO TERMINAL STRIP
| 1ST FL | [8 empty] | AV
| AV | [8 empty] | 4TH FL
| AV | [8 empty] | AV
| AV | [8 empty] | AV | RED + OUT BLACK - OUT, YELLOW + RETURN GREEN - RETURN
| AV |  | RETURN NAC1 TO FACP ON YELLOW-GREEN TO TERMINAL STRIP | [6 empty] | ROOF
|  |  | EOL AT FACP TERMINAL STRIP | [6 empty] | WP AV
RETURN NAC2 TO FACP ON YELLOW-GREEN TO TERMINAL STRIP
EOL AT FACP TERMINAL STRIP