Director of Planning and Urban Development

Penny St. Louis Littell

Inspection Services, Director

Tammy M. Munson

October 7, 2009

CONNOLLY CAROL A

42 MELBOURNE ST

PORTLAND , ME  04101

CBL: 014  L007001						Certified Mail70080500000145878454

Located at 42 MELBOURNE ST

SECOND NOTICE OF VIOLATION- BILLING NOTIFCATION

Dear Carol A. Connolly:

A re-evaluation of the above stated property on 10/06/09 revealed that this office has no record of an HVAC permit being issued to this location. Furthermore, the location of the newly installed mechanical direct-vent does not comply with the City Code.

The property is in violation of the International Mechanical Code, 2003 as stated below:

Section 804.3.4 (3). Horizontal terminations.

- Where located adjacent to walkways, the termination of mechanical draft systems shall be not less than seven (7) feet from above the level of the walkway.

- The vent system shall terminate at least four (4) feet below, four (4) feet horizontally from or one (1) foot above any door, window or gravity air inlet into the building.

An HVAC permit application must be submitted to this office within five (5) days of the date of this notice. Failure to comply will result in this office referring the matter to the City of Portland Corporation Counsel for legal action and possible civil penalties, as provided for in § 1-15 of the Code.

Please be advised that because this is the second inspection and there are repeat violations, § 6.2 of the Code requires that you pay a $175.00 re-inspection/ after-the-fact permitting fee.  This must be paid prior to re-inspection. Failure to pay the assessed fee within thirty (30) days shall cause the City to assess lien against the property pursuant to § 1-16 of the Code

This constitutes an appealable decision pursuant to § 6-127 of the Code.

If you have any questions or concerns please feel free to contact me at 207.874.8702.

Sincerely,

Jon Rioux,

Code Enforcement Officer

CC: Tammy M. Munson, Inspection Services Division Director