From: 	Chris Pirone
To:	Donaldson, Helen
Date: 	8/2/2013 7:16 AM
Subject: 	Re: Bay House Phase II

Nell,

Initial comments:
Addition of sidewalk for continuation of Exit Access looks good.

Waiting on how team:

1. Address emergency access to rear of parking lot.
Options:
A. Increase Vertical clearance to 13'6 of entrance
B. Provide Fire Protection(standpipe) for vehicle fires in rear of parking area.

2. The address/addresses for the project

3. Updated NFPA 101 and City Chapter 10 Code analysis as the Architect stated he just copied over the one used for the first phase.

4. Location of FDC for building sprinkler system. 

Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410

>>> Helen Donaldson 07/29/13 9:34 AM >>>
Chris, 
 
Here are revised plans from Will Conway.  Much better than what we were working with before.  
 
Can you let me know if you have additional comments?  I'm am trying to finish up a memo to the Board by end of day Thursday.  I know that's kind of a tight deadline, but if you can squeeze a quick look in, that would be great.
 
Thanks, Chris.  
 
Nell