From: 	Chris Pirone
To:	Helen Donaldson
Date: 	9/6/2013 8:15 AM
Subject: 	Re: Bay House Phase II

1. Sprinkler Connection(FDC) can not be in entry vestibule.
2. What is the address situation?
3. I see the standpipe connection. It will most likely be impractical for the installers and will end up near the stair.
 
Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410
 
ü Please consider the environment before printing this email.

>>> Helen Donaldson 9/5/2013 11:09 AM >>>
Chris, 
 
I just wanted to follow up from yesterday on Bay House Phase II.  Their revised submittal includes a bunch of stuff related to fire, which I thought I'd pass along.  
 
Attached are:
- 2 revised code analyses
- revised site plan, showing standpipe at building's rear and connections near entry vestibule on Newbury Street
 
Can you let me know if you need further changes or if this is okay?
 
Thanks!
Nell