Copyright 1996, The American Institute of Architects (AIA)

SECTION 08334

OVERHEAD COILING GRILLES

GENERAL

SUMMARY

This Section includes the following:

Electric-motor-operated overhead coiling grilles.

Related Sections include the following:

List below only products, construction, and equipment for this Project that the reader might expect to find in this Section but are specified elsewhere.  Verify that Section titles listed below are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

Division 16 Sections for electrical service and connections for powered operators, and accessories.

DEFINITIONS

Retain definition per national association of garage door manufacturers below if "Performance Requirements" Article is retained.

Operation Cycle:  One complete cycle of a grille begins with the grille in the closed position.  The grille is then moved to the open position and back to the closed position.

PERFORMANCE REQUIREMENTS

Select 1 of 2 paragraphs below or revise to suit products selected.  Revise value to 50,000 or 100,000 for higher-cycle operation, corrosive environments, and severe or abusive use.  Cycles per fixed time can also be used to more stringently define operation performance.  Cookson standard value is 50,000 cycles and 25 cycles per day.

Paragraph above is standard with some manufacturers.  Paragraph below is more commonly used standard.  Cycles per fixed time can also be used to more stringently define operation performance.

Operation-Cycle Requirements:  Design overhead coiling grille components and operator to operate for not less than 50,000 cycles.

SUBMITTALS

Product Data:  For each type and size of overhead coiling grille and accessory.  Include details of construction relative to materials, dimensions of individual components, profiles, and finishes.  Provide roughing-in diagrams, operating instructions, and maintenance information.  Include the following:

Setting drawings, templates, and installation instructions for built-in or embedded anchor devices.

Walls and jambs must be designed to support grille.  Retain subparagraph below unless information has already been determined and does not need to be confirmed.

Summary of forces and loads on walls and jambs.

Motors:  Show nameplate data and ratings; characteristics; mounting arrangements; size and location of winding termination lugs, conduit entry, and grounding lug; and coatings.

Shop Drawings:  For special components and installations not dimensioned or detailed in manufacturer's data sheets.

Delete paragraph above if not required.  Delete subparagraph below if no components include wiring.

Wiring Diagrams:  Detail wiring for power, signal, and control systems.  Differentiate between manufacturer-installed and field-installed wiring and between components provided by grille manufacturer and those provided by others.

Retain 2 sample paragraphs below for colored products and products with factory-applied decorative finishes.  Delete if not required.

Samples for Selection:  Manufacturer's color charts showing the full range of colors available for units with factory-applied finishes.

Delete above if colors are preselected and specified or scheduled.  Retain below with or without above.

Retain below if Installer certification is required in "Quality Assurance" Article.

Qualification Data:  For Installer.

QUALITY ASSURANCE

Installer Qualifications:  Engage an experienced installer who is an authorized representative of the overhead coiling grille manufacturer for both installation and maintenance of units required for this Project.

Source Limitations:  Obtain overhead coiling grilles through one source from a single manufacturer.

Delete subparagraph below if no operators and controls or if not required.  Revise if no controls.

Obtain operators and controls from the overhead coiling grille manufacturer.

Delete paragraph and subparagraphs below if no motorized operator.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100.

PRODUCTS

MANUFACTURERS

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

Revise list of manufacturers below to suit Project.

The Cookson Company.

Cornell Iron Works, Inc.

Overhead Door Corporation.

Raynor Garage Doors.

Wayne-Dalton Corp.

GRILLE CURTAIN MATERIALS AND CONSTRUCTION

General:  Fabricate overhead coiling grille curtain consisting of a network of 5/16-inch (8-mm) minimum diameter horizontal rods, or rods covered with tube spacers, spaced as indicated.  Interconnect rods by vertical links approximately 5/8 inch (16 mm) wide, spaced as indicated and rotating on rods.

Space rods at approximately 3 inches (76 mm) o.c.

Select one spacing from subparagraphs above and one spacing from subparagraphs below, or revise.  Spacings are not common to all manufacturers.

Below is straight in-line pattern common to manufacturers listed.  Revise to suit Project and verify availability with manufacturers listed if another pattern is required.

Space links in line at approximately 9 inches (228 mm) apart.

Select one grille material below and delete others, or revise to suit Project.  Verify availability with manufacturers selected.

Aluminum Grilles:  ASTM B 221 (ASTM B 221M), alloy and temper recommended by aluminum producer and finisher for type of use and finish indicated.

Endlocks:  Continuous end links, chains, or other devices at ends of rods, locking and retaining grille curtain in guides against excessive pressures, maintaining curtain alignment, and preventing lateral movement.

Bottom Bar:  Manufacturer's standard continuous channel, tubular shape, or 2 angles, finished to match grille.

Astragal:  Provide a replaceable, adjustable, continuous, compressible gasket of flexible vinyl, rubber, or neoprene, between angles or fitted to shape, as a cushion bumper for interior grille.

Delete subparagraph below if not required.

Provide motor-operated grilles with combination bottom astragal and sensor edge.

Curtain Jamb Guides:  Manufacturer's standard extruded-aluminum shape having curtain groove with return lips or bars to retain curtain.  Provide continuous integral wear strips to prevent metal-to-metal contact and minimize noise of travel.  Provide removable stops on guides to prevent overtravel of curtain.

Not all manufacturers offer option below.

HOODS AND ACCESSORIES

Delete paragraph below if curtain and operating mechanism are concealed in soffit.

Hood:  Form to entirely enclose coiled curtain and operating mechanism at opening head.  Contour to suit end brackets to which hood is attached.  Roll and reinforce top and bottom edges for stiffness.  Provide closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting projecting beyond wall face.  Provide intermediate support brackets as required to prevent sag.

Select hood type(s) required; delete others.

Fabricate aluminum hoods, complying with ASTM B 209 (ASTM B 209M), alloy and temper recommended by aluminum producer and finisher for type of use and finish indicated, and not less than 0.032 inch (0.8 mm) thick, for aluminum grilles.

Shape:  Round or square.

Delete subparagraph above or below.  Above is standard.  Verify below, which is available for service grilles, with manufacturer.

Retain subparagraph below for concealed installations.  Metal soffit is not often used.  Show on Drawings.

Provide removable metal soffit when hood is mounted above ceiling of same material and finish of curtain, unless otherwise indicated.

On west elevation, provide hood of extended length as shown on Elevation drawings.

Delete paragraph below if no push-up operated grilles or push-up emergency operation.

Push/Pull Handles:  For push-up-operated or emergency-operated grilles, provide lifting handles on each side of grille.

Delete subparagraph below if none.

Provide pull-down straps or pole hooks for grilles more than 84 inches (2130 mm) high.

Slide Bolt:  Fabricate with side locking bolts to engage through slots in tracks for locking by padlock, located on single-jamb side, operable from coil side.

Paragraph above is standard for push-up grilles.  Revise above if no padlock or if manufacturer's standard is bolt on both sides.  Paragraph below describes locking device with choice of location and operation; coordinate with cylinder selected.  Retain above or below or both, and revise to suit Project.

Retain paragraph below for chain-hoist operator or emergency chain-hoist operation.

Delete paragraph below if no power-operated grilles.

Where grille unit is power operated, provide safety interlock switch to disengage power supply when grille is locked.

Method of mounting below, available from some manufacturers, is optional to allow fast-track installation of grille before wall and opening are built.

Mounting Tube Frame:  Provide manufacturer's standard mounting tube frame designed to support grille; factory fabricated from structural-steel tubes; fastened to floor and structure above grille; to be built into wall construction; and complete with anchors, connections, and fasteners.

COUNTERBALANCING MECHANISM

General:  Counterbalance grille by means of adjustable-tension steel helical torsion spring, mounted around a steel shaft and contained in a spring barrel connected to the curtain.  Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

Counterbalance Barrel:  Fabricate spring barrel of hot-formed, structural-quality, welded or seamless carbon-steel pipe, of sufficient diameter and wall thickness to support rolled-up curtain without distortion of curtain and to limit barrel deflection to not more than 0.03 in./ft. (2.5 mm/m) of span under full load.

Provide spring balance of one or more oil-tempered, heat-treated steel helical torsion springs.  Size springs to counterbalance weight of curtain, with uniform adjustment accessible from outside barrel.  Provide cast-steel barrel plugs to secure ends of springs to barrel and shaft.

Fabricate torsion rod for counterbalance shaft of case-hardened steel, sized to hold fixed spring ends and carry torsional load.

Brackets:  Provide mounting brackets of manufacturer's standard design, either cast-iron or cold-rolled steel plate.

ELECTRIC GRILLE OPERATORS

Delete this Article if no electric operators.  Retain for larger units, remote control, frequent operation, or complex mounting conditions.

Delete "and operational life" below if none is required in Part 1.

General:  Provide electric grille operator assembly of size and capacity recommended and provided by grille manufacturer for grille and operational life specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, remote-control stations, control devices, integral gearing for locking grille, and accessories required for proper operation.

Comply with NFPA 70.

Disconnect Device:  Provide hand-operated disconnect or mechanism for automatically engaging sprocket-chain operator and releasing brake for emergency manual operation while disconnecting motor, without affecting timing of limit switch.  Mount disconnect and operator so they are accessible from floor level.  Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

Design operator so motor may be removed without disturbing limit-switch adjustment and without affecting emergency auxiliary operator.

Provide control equipment complying with NEMA ICS 1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24-V, ac or dc.  Coordinate connection of grill operation to the ‘AVI’ (Automatic Vehicle Identification) and access control system.

Paragraph above and below are examples only.  Delete above if grille exceeds 96 inches (2400 mm) in height.  Delete below if no auxiliary chain hoist.  Refer to manufacturer's data for particular applications.

Grille-Operator Type:  Provide wall-, hood-, or bracket-mounted, jackshaft, gear-head hoist-type grille operator unit consisting of electric motor, enclosed worm-gear running-in-oil primary drive, chain and sprocket secondary drive, and auxiliary chain hoist and floor level disconnect.

Rate below is for standard-speed grilles.  Consult manufacturer and revise for high-speed operation.

Electric Motors:  Provide high-starting torque, reversible, continuous-duty, Class A insulated, electric motors, complying with NEMA MG 1, with overload protection, sized to start, accelerate, and operate grille in either direction, from any position, at not less than 2/3 fps (0.2 m/s) and not more than 1 fps (0.3 m/s), without exceeding nameplate ratings or considering service factor.

Revise subparagraph below for single-phase, capacitor-start type or other variation of motor less than 1/2 hp.  See Evaluations.  Verify electrical characteristics with electrical engineer.

Type:  Polyphase, medium-induction type.

Service Factor:  According to NEMA MG 1, unless otherwise indicated.

Coordinate wiring requirements and electric characteristics of motors with building electrical system.

Select type of motor or revise description to suit Project.  If more than one type is required, show each type on Drawings.

Provide open dripproof-type motor, and controller with NEMA ICS 6, Type 1 enclosure.

Use subparagraph below for exterior, wet, or humid installations.

Revise paragraph below to suit Project.  A sustained-pressure switch may be required for closing and/or opening cycles.  Verify with authorities having jurisdiction.

Remote-Control Station:  Provide momentary-contact, 3-button control station with push-button controls labeled "Open," "Close," and "Stop."

Provide interior units, full-guarded, surface-mounted, heavy-duty type, with general-purpose NEMA ICS 6, Type 1 enclosure.

Delete subparagraph below if none or revise to suit Project.  Also use for wet or humid conditions.

Provide exterior units, full-guarded, standard-duty, surface-mounted, weatherproof type, NEMA ICS 6, Type 4 enclosure, key operated.

Coordinate controls with security and access control systems.

Delete paragraph below if not required or revise to suit Project.

Obstruction Detection Device:  Provide each motorized grille with indicated external automatic safety sensor able to protect full width of grille opening.  Activation of sensor immediately stops and reverses downward grille travel.

Select 1 of 2 sensor types below.

Sensor Edge:  Provide each motorized grille with an automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar.  Contact with sensor immediately stops and reverses downward grille travel.  Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

Delete subparagraph above or below.  Above may be limited to 18-foot (5.5-m) width.  Verify with manufacturers selected.  See Evaluations for description.

Provide electrically actuated automatic bottom bar.

Delete subparagraph below if standard 2-wire device is acceptable and no self-monitoring system to detect failure of sensor device is required.

Self-Monitoring Type:  Provide self-monitoring, 4-wire configured device.

Limit Switches:  Provide adjustable switches, interlocked with motor controls and set to automatically stop grille at fully opened and fully closed positions.

Provide electric operators with ADA-compliant audible alarm and visual indicator lights.

Delete paragraph above if none.  Verify requirement below with authorities having jurisdiction.

FINISHES, GENERAL

General:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

Appearance of Finished Work:  Variations in appearance of abutting or adjacent pieces are acceptable if they are within one-half of the range of approved Samples.  Noticeable variations in the same piece are not acceptable.  Variations in appearance of other components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

ALUMINUM FINISHES

Delete this Article if no aluminum components.

Finish designations prefixed by AA conform to the system established by the Aluminum Association for designating aluminum finishes.

Retain one finish below.

Manufacturer's standard mill finish.

Revise below for color-anodized finish.  Verify with manufacturers selected.

Class II, Clear Anodic Finish:  AA-M12C22A31 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class II, clear coating 0.010 mm or thicker) complying with AAMA 607.1.

Revise Article title below if galvanized surfaces are not finish painted.  Always retain priming of bare steel.

EXECUTION

INSTALLATION

General:  Install grilles and operating equipment complete with necessary hardware, according to Shop Drawings, manufacturer's written instructions, and as specified.

ADJUSTING

Lubricate bearings and sliding parts; adjust grilles to operate easily, free from warp, twist, or distortion and fitting tight for entire perimeter.

DEMONSTRATION

Startup Services:  Engage a factory-authorized service representative to perform startup services and to train Owner's maintenance personnel as specified below.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Train Owner's maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, preventive maintenance, and procedures for testing and resetting release devices.

Review data in the maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.

Review data in the maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

Schedule training with Owner with at least 7 days' advance notice.

END OF SECTION