- SECTION 10520 – FIRE PROTECTION SPECIALTIES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- PART 1 - GENERAL

1.1	RELATED DOCUMENTS

A. 	Site drawings produced by Pinkham and Greer Consulting Engineers, foundation/basement plan drawings produced by TFH Architects PA and Structural Design Consulting, building drawings produced by TFH Architects, mechanical drawings produced by TFH Architects, electrical and lighting drawings produced by TFH Architects.  Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections apply to all sections.

1.2		SUMMARY

- This Section includes the following:

  - Portable fire extinguishers.  (Provide one each mechanical room; six total)

  - Mounting brackets for fire extinguishers

  - SUBMITTALS

A.	Product data:  Include construction details, material descriptions, dimensions of individual components and profiles.

- Fire extinguishers:  Include rating and classification.

- Maintenance data:  For fire extinguishers and fire-protection cabinets to include in maintenance manuals.

1.4	QUALITY ASSURANCE

A.	Source limitations:  Obtain fire extinguishers and fire-protection cabinets through one source from a single manufacturer.

B.	NFPA compliance:  Fabricate and label fire extinguishers to comply with NFPA 10, “Portable Fire Extinguishers.”

- Fire extinguishers:  Listed and labeled for type, rating and classification by an independent testing agency acceptable to authorities having jurisdiction.

1.	Provide fire extinguishers approved, listed and labeled by FMG.

1.5	COORDINATION

A.	Coordinate size of fire-protection cabinets to ensure that type and capacity of fire extinguishers indicated are accommodated.

PART 2 – PRODUCTS

  - MANUFACTURERS

A.	In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

- Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

  - MATERIALS

A.	Cold-rolled steel sheet:  ASTM A 1008/A 1008M, Commercial Steel (CS), Type B.

B.	Aluminum:  Alloy and temper recommended by aluminum producer and manufacturer for type of use and finish indicated, and as follows:

- Sheet:  ASTM B 209 (ASTM B 209M).

- Extruded shapes:  ASTM B 221 (ASTM B 221M).

C.	Clear float glass:  ASTM C 1036, Type 1, Class 1, Quality q3, 6 mm thick.

2.3	PORTABLE FIRE EXTINGUISHERS

A.	Manufacturers:

1.		Amerex Corporation.

2.		JL Industries, Inc.

3.		Larsen’s Manufacturing Company.

4.		Potter Roemer; Div. of Smith Industries, Inc.

B.	General:  Provide fire extinguishers of type, size and capacity for each fire-protection cabinet and mounting bracket indicated.

C.	Multi-purpose dry chemical type in aluminum container:  UL-rated 4-A: 60b;c, 10-lb. (4.5-kg) nominal capacity, with monoammonium phosphate-based dry chemical in manufacturer’s standard aluminum container.

2.4	MOUNTING BRACKETS

A.	Manufacturers:

1.		Amerex Corporation.

2.		JL Industries, Inc.

3.		Larsen’s Manufacturing Company.

4.		Potter Roemer; Div. of Smith Industries, Inc.

B.	Mounting brackets:  Manufacturer’s standard galvanized steel, designed to secure fire extinguisher to wall or structure, of sizes required for types and capacities of fire extinguishers indicated, with plated or baked-enamel finish.

1.		Color:  black.

C.	Identification:  Lettering complying with authorities having jurisdiction for letter style, size, spacing and location.  Locate as indicated by architect.

1.	Identify bracket-mounted fire extinguishers with the words “FIRE EXTINGUISHER” in red letter decals applied to mounting surface.

a.	Orientation:  Horizontal.

2.5	FINISHES, GENERAL

A.	Comply with NAAMM’s “Metal Finishes Manual for Architectural and Metal Products” for recommendations for applying and designating finishes.

B.	Protect mechanical finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

PART 3 – EXECUTION

  - EXAMINATION

A.	Examine fire extinguishers for proper charging and tagging.

- Remove and replace damaged, defective or undercharged units.

B.	Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

A.	General:  Install fire-protection specialties in locations and at mounting heights indicated or, if not indicated, at heights indicated below:

- Mounting brackets:  54 inches (1372 mm) above finished floor to top of fire extinguisher.

B.	Mounting brackets:  Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

C.	Identification:  Apply vinyl lettering at locations indicated.

  - ADJUSTING AND CLEANING

A.	Remove temporary protective coverings and strippable films, if any, as fire-protection specialties are installed, unless otherwise indicated in manufacturers written installation instructions.

- END OF SECTION 10520