# SECTION 08110 - STEEL DOORS AND FRAMES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

# PART 1 - GENERAL

# 1.1	RELATED DOCUMENTS

A.	Site drawings produced by Pinkham and Greer Consulting Engineers, foundation/basement plan drawings produced by TFH Architects PA and Structural Design Consulting, building drawings produced by TFH Architects, mechanical drawings produced by TFH Architects, electrical and lighting drawings produced by TFH Architects.  Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections apply to all sections.

# 1.2	SUMMARY

A.	This Section includes the following:

Adjust list below to suit Project.

1.	Steel doors.

2.	Steel door frames.

3.	Fire-rated door and frame assemblies.

4.	Custom steel door frames, rated and non-rated.

B.	Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1.	Division 4 Section "Unit Masonry Assemblies" for installing anchors and grouting frames in masonry construction.

2.	Division 6 Section “Finish Carpentry” for wood trim applied to steel frames.

3.	Division 8 Section "Flush Wood Doors" for wood doors installed in steel frames.

4.	Division 8 Section "Door Hardware (Scheduled by Naming Products)" for door hardware and weather stripping.

6.	Division 8 Section "Glazing" for glass in glazed openings in doors and frames.

8.	Division 9 Section "Painting" for field painting factory-primed doors and frames.

# 1.3	DEFINITIONS

A.	Steel Sheet Thicknesses:  Thickness dimensions, including those referenced in ANSI A250.8, are minimums as defined in referenced ASTM standards for both uncoated steel sheet and the uncoated base metal of metallic-coated steel sheets.

# 1.4	SUBMITTALS

A.	Product Data:  For each type of door and frame indicated, include door designation, type, level and model, material description, core description, construction details, label compliance, sound and fire-resistance ratings, and finishes.

Usually delete paragraph and subparagraphs below.  The intent of this Section is that doors and frames comply with ANSI A250.8; therefore, Shop Drawings are not required.

B.	Shop Drawings:  Show the following:

Delete subparagraphs below for doors if this Section is edited to include only steel frames for wood doors.

1.	Elevations of each door design.

2.	Details of doors including vertical and horizontal edge details.

3.	Frame details for each frame type including dimensioned profiles.

4.	Details and locations of reinforcement and preparations for hardware.

5.	Details of each different wall opening condition.

6.	Details of anchorages, accessories, joints, and connections.

- Coordination of glazing frames and stops with glass and glazing requirements.

- Field verify existing conditions for frame installation during shop drawing preparation.

C.	Door Schedule:  Use same reference designations indicated on Drawings in preparing schedule for doors and frames.

Delete below if not required.

# 1.5	QUALITY ASSURANCE

Retain paragraph below and other references to ANSI A250.8 for quality control.

A.	Steel Door and Frame Standard:  Comply with ANSI A 250.8, unless more stringent requirements are indicated.

Delete paragraph below if not applicable.

B.	Fire-Rated Door Assemblies:  Assemblies complying with NFPA 80 that are listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire-protection ratings indicated, based on testing according to NFPA 252.

Revise subparagraph below if positive-pressure testing is required.

# 1.6	DELIVERY, STORAGE, AND HANDLING

A.	Deliver doors and frames cardboard-wrapped or crated to provide protection during transit and job storage.  Provide additional protection to prevent damage to finish of factory-finished doors and frames.

B.	Inspect doors and frames on delivery for damage, and notify shipper and supplier if damage is found.  Minor damages may be repaired provided refinished items match new work and are acceptable to Architect.  Remove and replace damaged items that cannot be repaired as directed.

C.	Store doors and frames at building site under cover.  Place units on minimum 4-inch high wood blocking.  Avoid using non-vented plastic or canvas shelters that could create a humidity chamber.  If door packaging becomes wet, remove cartons immediately.  Provide minimum 1/4-inch spaces between stacked doors to permit air circulation.

# PART 2 - PRODUCTS

# 2.1	MANUFACTURERS

A.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Product Requirements."

B.	Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1.	Steel Doors andFrames:

a.	Amweld Building Products, Inc.

b.	Benchmark Commercial Doors; a division of General Products Co., Inc.

c.	Ceco Door Products; a United Dominion Company.

d.	Copco Door Co.

e.	Curries Company.

f.	Deansteel Manufacturing, Inc.

g.	Kewanee Corporation (The).

h.	Mesker Door, Inc.

i.	Pioneer Industries Inc.

j.	Republic Builders Products.

k.	Steelcraft; a division of Ingersoll-Rand.

# 2.2	MATERIALS

A.	Hot-Rolled Steel Sheets:  ASTM A 569/A 569M, Commercial Steel (CS), Type B; free of scale, pitting, or surface defects; pickled and oiled.

B.	Cold-Rolled Steel Sheets:  ASTM A 366/A 366M, Commercial Steel (CS), or ASTM A 620/A 620M, Drawing Steel (DS), Type B; stretcher-leveled standard of flatness.

Retain first paragraph below for exterior units or if required in high-humidity areas.

C.	Metallic-Coated Steel Sheets:  ASTM A 653/A 653M, Commercial Steel (CS), Type B, with an A40 zinc-iron-alloy (galvannealed) coating; stretcher-leveled standard of flatness.

# 2.3	DOORS AND TRANSOM PANELS

Refer to SDI 108 for recommended selection and usage guides.  Select levels and models.  See tables in the Evaluations for more information.

A.	General:  Provide doors of sizes, thicknesses, and designs indicated.

B.	Interior Doors and Transom Panels:  Provide doors complying with requirements indicated below by referencing ANSI 250.8 for level and model and ANSI A250.4 for physical-endurance level:

Retain one or more levels and models below.  If more than one level and model are retained, indicate in a door and frame schedule on Drawings where each is required.

Level 1 doors above have 0.032-inch- (0.8-mm-) thick faces and apply to both 1-3/8- and 1-3/4-inch- (34.9- and 44.4-mm-) thick doors.  Level 2 doors below have 0.042-inch- (1.0-mm-) thick faces and apply only to 1-3/4-inch- (44.4-mm-) thick doors.

1.	Level 2 and Physical Performance Level B (Heavy Duty 19 gauge), Model 2 Seamless.

Level 3, Models 1, 2, and 3, doors below have 0.053-inch- (1.3-mm-) thick faces and apply only to 1-3/4-inch- (44.4-mm-) thick doors.

C.	Exterior Doors:  Provide doors complying with requirements indicated below by referencing ANSI A250.8 for level and model and ANSI A250.4 for physical-endurance level:

1.	Level 3 and Physical Performance Level A (Extra Heavy Duty 16 gauge), Model 2 Seamless.

Level 3, Models 1, 2, and 3, doors above have 0.053-inch- (1.3-mm-) thick faces.  Level 4, Models 1 and 2, doors below have 0.067-inch- (1.7-mm-) thick faces.

Delete paragraph and subparagraphs below if door louvers are not required or revise to include other types, such as pierced louvers, adjustable louvers, air grilles, and galvanized exterior louvers with insect screens.

D.	Vision Lite Systems:  Manufacturer's standard kits consisting of glass lite moldings to accommodate glass thickness and size of vision lite indicated.

E.	Panels shall be of same material, construction and finish as specified for doors.

# 2.4	STANDARD AND CUSTOM FRAMES

A.	General:  Provide steel frames for doors, transoms, sidelights, borrowed lights, and other openings that comply with ANSI A250.8 and with details indicated for type and profile.  Conceal fastenings, unless otherwise indicated.

If more than one frame thickness is required for each steel door level or for each different type of wood door, retain the optional phrase ", unless otherwise indicated" for the frame thickness that is the default, and retain the optional phrase "where indicated" for the frame thickness whose location is indicated on Drawings, generally in a door and frame schedule.

B.	Frames of 0.053-inch- (16 gauge) thick steel sheet for:

1.	Level 2 steel doors.

2.	Interior wood doors where standard steel frames are indicated.

C.	Frames of 0.067-inch- (14 gauge) thick steel sheet for:

1.	Level 3 steel doors, unless otherwise indicated galvanized.

D.	Door Silencers:  Except on weather-stripped frames, fabricate stops to receive three silencers on strike jambs of single-door frames and two silencers on heads of double-door frames.

E.	Plaster Guards:  Provide 0.016-inch- (28 gauge) thick, steel sheet plaster guards or mortar boxes to close off interior of openings; place at back of hardware cutouts where mortar or other materials might obstruct hardware operation.

F.	Supports and Anchors:  Fabricated from not less than 0.042-inch- (18 gauge) thick, electrolytic zinc-coated or metallic-coated steel sheet.

G.	Inserts, Bolts, and Fasteners:  Manufacturer's standard units.  Where zinc-coated items are to be built into exterior walls, comply with ASTM A 153/A 153M, Class C or D as applicable.

# 2.5	FABRICATION

A.	General:  Fabricate steel door and frame units to comply with ANSI A250.8 and to be rigid, neat in appearance, and free from defects including warp and buckle.  Where practical, fit and assemble units in manufacturer's plant.  Clearly identify work that cannot be permanently factory assembled before shipment, to assure proper assembly at Project site.

Delete first paragraph below if not required.  Revise to suit Project.  If doors fabricated from metallic-coated steel sheet are required at other than exterior locations because of high-humidity or corrosive interior environments, indicate locations on Drawings or insert descriptions here.

B.	Exterior Door Construction:  For exterior locations and elsewhere as indicated, fabricate doors, panels, and frames from metallic-coated steel sheet.  Close top and bottom edges of doors flush as an integral part of door construction or by addition of 0.053-inch- (1.3-mm-) thick, metallic-coated steel channels with channel webs placed even with top and bottom edges.

C.	Interior Door and Panel Faces:  Fabricate exposed faces of doors and panels, including stiles and rails of nonflush units, from the following material:

1.	Cold-rolled steel sheet, unless otherwise indicated.

If both cold-rolled steel sheet above and optional metallic-coated steel sheet below are retained and the latter is the default requirement, retain optional text above and indicate on Drawings where doors faced with metallic-coated steel sheet are required.

D.	Core Construction:  Manufacturer's standard core construction that produces a door complying with SDI standards.

Delete paragraph above or below.  Retain below with selected core constructions.

E.	Clearances for Non-Fire-Rated Doors:  Not more than 1/8 inch at jambs and heads, except not more than 1/4 inch between pairs of doors.  Not more than 3/4 inch at bottom.

F.	Clearances for Fire-Rated Doors:  As required by NFPA 80.

If more than one edge profile is required, retain one edge profile as default and indicate on Drawings where other edge profile occurs.

G.	Single-Acting, Door-Edge Profile:  Beveled edge.

Verify availability of door-edge profile below in standard steel doors from manufacturers selected.  This profile is not recognized in ANSI A250.8.

H.	Tolerances:  Comply with SDI 117, "Manufacturing Tolerances for Standard Steel Doors and Frames."

I.	Fabricate concealed stiffeners, reinforcement, edge channels, louvers, and moldings from either cold- or hot-rolled steel sheet.

J.	Exposed Fasteners:  Unless otherwise indicated, provide countersunk flat or oval heads for exposed screws and bolts.

Delete paragraph and subparagraph below if not required.

K.	Thermal-Rated (Insulating) Assemblies:  At exterior locations and elsewhere as shown or scheduled, provide doors fabricated as thermal-insulating door and frame assemblies and tested according to ASTM C 236 or ASTM C 976 on fully operable door assemblies.

Revise value below as required.

1.	Unless otherwise indicated, provide thermal-rated assemblies with U-value of .036 Btu/sq. ft. x h x deg F or better.

Delete paragraph and subparagraph below if not required.

L.	Hardware Preparation:  Prepare doors and frames to receive mortised and concealed hardware according to final door hardware schedule and templates provided by hardware supplier.  Comply with applicable requirements in ANSI A250.6 and ANSI A115 Series specifications for door and frame preparation for hardware.

Delete subparagraph below if no concealed overhead closers.

M.	Frame Construction:  Fabricate frames to shape shown.

Retain one or more of first four subparagraphs below to suit Project.  According to ANSI A250.8, seamless face joints are only provided if specified.

1.	Fabricate frames with mitered or coped and continuously welded corners and seamless face joints.

4.	For exterior applications, fabricate frames with mitered or coped and continuously welded corners and seamless face joints.

Delete subparagraph below if not required.  According to ANSI A250.8, temporary spreader bars for welded frames will only be provided if specified and are intended for shipping and handling purposes only.

6.	Provide welded frames with temporary spreader bars.

Delete subparagraph below if not required.  According to ANSI A250.8, terminated stops will only be provided if specified.

N.	Reinforce doors and frames to receive surface-applied hardware.  Drilling and tapping for surface-applied hardware may be done at Project site.

O.	Locate hardware as indicated on Shop Drawings or, if not indicated, according to ANSI A250.8.

P.	Glazing Stops:  Manufacturer's standard, formed from 0.032-inch- (20 gauge) thick steel sheet.

1.	Provide nonremovable stops on outside of exterior doors and on secure side of interior doors for glass, louvers, and other panels in doors.

2.	Provide screw-applied, removable, glazing stops on inside of glass, louvers, and other panels in doors.

Delete below if no pairs of doors with fire ratings of more than one-and-one-half hours or if no pairs of doors requiring astragals for fire ratings.

T.	Astragals:  As required by NFPA 80 to provide fire ratings indicated.

# 2.6	FINISHES

# A.	Prime Finish:  Manufacturer's standard, factory-applied coat of rust-inhibiting primer complying with ANSI A250.10 for acceptance criteria.

Delete paragraph above if paragraph below is retained and all doors and frames are required to have factory-applied paint finish.  If only selected doors and frames are to have one of the other finishes, make one requirement the default and indicate on Drawings which doors and frames receive the other finish. Correlate with Division 9 Section "Painting."

# B.	Factory-Applied Paint Finish:  Manufacturer's standard, factory-applied paint finish complying with ANSI A250.3 for performance and acceptance criteria.

Retain one color and gloss below.

1.	Color and Gloss:  As selected by Architect from manufacturer's full range.

# PART 3 - EXECUTION

# 3.1	INSTALLATION

A.	General:  Install steel doors, frames, and accessories according to Shop Drawings, manufacturer's data, and as specified.

B.	Placing Frames:  Comply with provisions in SDI 105, unless otherwise indicated.  Set frames accurately in position, plumbed, aligned, and braced securely until permanent anchors are set.  After wall construction is completed, remove temporary braces and spreaders, leaving surfaces smooth and undamaged.

1.	Except for frames located in existing walls or partitions, place frames before construction of enclosing walls and ceilings.

Edit subparagraphs below to suit Project.

2.	In masonry construction, provide at least three wall anchors per jamb; install adjacent to hinge location on hinge jamb and at corresponding heights on strike jamb.  Acceptable anchors include masonry wire anchors and masonry T-shaped anchors.

3.	In existing concrete or masonry construction, provide at least three completed opening anchors per jamb; install adjacent to hinge location on hinge jamb and at corresponding heights on strike jamb.  Set frames and secure to adjacent construction with bolts and masonry anchorage devices.

4.	In metal-stud partitions, provide at least three wall anchors per jamb; install adjacent to hinge location on hinge jamb and at corresponding heights on strike jamb.  Attach wall anchors to studs with screws.

5.	For in-place gypsum board partitions, install knock-down, drywall slip-on frames.

6.	Install fire-rated frames according to NFPA 80.

7.	For openings 90 inches (2286 mm) or more in height, install an additional anchor at hinge and strike jambs.

C.	Door Installation:  Comply with ANSI A250.8.  Fit hollow-metal doors accurately in frames, within clearances specified in ANSI A250.8.  Shim as necessary to comply with SDI 122 and ANSI/DHI A115.1G.

Retain applicable subparagraphs below.

1.	Fire-Rated Doors:  Install within clearances specified in NFPA 80.

2.	Smoke-Control Doors:  Install to comply with NFPA 105.

# 3.2	ADJUSTING AND CLEANING

A.	Prime-Coat Touchup:  Immediately after installation, sand smooth any rusted or damaged areas of prime coat and apply touch up of compatible air-drying primer.

B.	Protection Removal:  Immediately before final inspection, remove protective wrappings from doors and frames.

# END SECTION 08110