## Power Supply Config
|  |  | Project Name: |  | Portland High School |  | Standby Hours: |  | 24
|  |  | Project ID: |  |  |  | Alarm Mins: |  | 5
|  |  | Prepared By: |  | Kevin Inman |  | Derating Factor: |  | 1.2
SK5895XL Calculations |  |  |  | Date: | 2016-06-28 |  | Voltage Drop Warning Threshold % :
Version 10.24.14 | [8 empty] | 10
Panel ID: | 5895XL |  | Model: | 5895XL Power Expander |  |  | Max NAC Current: |  | 3.0 Amps
Location: | Ground floor FA101B |  | Volts: | 24 VDC |  |  | Max Panel Current: |  | 6.0 Amps
Part.# | Description | Qty | Current Draw |  | Wire AWG | Ohms Per | Length(ft) | Actual | Volts @ | %Drop
|  |  | Standby | Alarm | & Type | 1000 Ft. | One-Way | Ohms | EOL
5895XL | 5895XL Pwr Module | 1 | 0.04 | 0.16 | N/A
SK | Photo, Photo-T |  | 0 | 0
SK | Ion |  | 0 | 0
SK | Heat, Heat-HT |  | 0 | 0
SK | Heat ROR |  | 0 | 0
SK | Beam, Beam-T |  | 0 | 0
SK | Duct |  | 0 | 0
SK | Acclimate |  | 0 | 0
SK | FIRE-CO |  | 0 | 0
SK | Control |  | 0 | 0
SK | Relaymon-2 |  | 0 | 0
SK | Control-6 |  | 0 | 0
SK | Monitor, Minimon |  | 0 | 0
SK | Monitor-2 |  | 0 | 0
SK | Monitor-10 |  | 0 | 0
SK | Pull-SA, Pull-DA |  | 0 | 0
SK | Relay |  | 0 | 0
SK | Relay-6 |  | 0 | 0
SK | Zone |  | 0 | 0
SK | Zone-6 |  | 0 | 0
SK | Isolator |  | 0 | 0
B224BI | Isolator Base |  | 0 | 0
B200SR | Sounder Base |  | 0 | 0
B200S | Intelligent Sounder Base |  | 0 | 0
B200SR-LF | Low Freq Sounder Base |  | 0 | 0
B200S-LF | Low Freq Sounder Base |  | 0 | 0
B224RB | Relay Base |  | 0 | 0
RTS151 | Magnetic Remote Test |  | 0 | 0
RTS151KEY | Key Activated Test |  | 0 | 0
RA100Z | Remote LED |  | 0 | 0
5815XL | SLC Expander |  | 0 | 0
5860 | LCD Remote Annunc |  | 0 | 0
5824 | Serial/Parallel Module |  | 0 | 0
5496 | Power Expander |  | 0 | 0
5895XL | Power Expander |  | 0 | 0
5865-4 | LED Annunciator (4G) |  | 0 | 0
5865-3 | LED Annunciator (3G) |  | 0 | 0
5880 | LED Driver Module |  | 0 | 0
5883 | Relay Module |  | 0 | 0
EVS-SW24 | Switch Expander |  | 0 | 0
EVS-AMP | 50W, 100W, 125W |  | 0 | 0
EVS-RVM | Remote Voice Module |  | 0 | 0
EVS-100WBU | Backup Amp Card |  | 0 | 0
PGM-I/O #1 | Notification Appl Circuit | 0.947 | 0 | 0.947 | #12 Solid | 1.59 | 300 | 0.954 | 19.7685 | 3.096%
PGM-I/O #2 | Notification Appl Circuit | 0.662 | 0 | 0.662 | #14 Stranded | 2.52 | 300 | 1.512 | 18.8472 | 7.612%
PGM-I/O #3 | Notification Appl Circuit | 1.027 | 0 | 1.027 | #14 Stranded | 2.52 | 350 | 1.764 | 19.2322 | 5.724%
PGM-I/O #4 | Notification Appl Circuit | 0.662 | 0 | 0.662 | #14 Stranded | 2.52 | 250 | 1.26 | 20.4 | 0%
PGM-I/O #5 | Notification Appl Circuit | 0 | 0 | 0 | #14 Stranded | 2.52 |  | 0 | 20.4 | 0%
PGM-I/O #6 | Notification Appl Circuit | 0 | 0 | 0 | Total Alarm Current (Amps)
Total Standby Current (Amps) |  |  | 0.04 | 3.458 | Alarm Time In Minutes / 60 |  | (5 Mins)
Standby Time In Hours |  |  | 24 | 0.083333 | Total Alarm AH Required
Total Standby AH Required |  |  | 0.96 | 0.28817 | Command Shortcuts
Total Combined AH Required |  |  | 1.2482
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 1.4978
Note on F30: Auxiliary power standby draw is 1.7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on G30: Auxiliary power alarm draw is 7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on F26: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on G26: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on F32: Auxiliary power standby draw is 8 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G32: Auxiliary power alarm draw is 20 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F39: Auxiliary power Standby draw is 12 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on G39: Auxiliary power Alarm draw is 90 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on F40: Auxiliary power Standby draw is 50 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G40: Auxiliary power Alarm draw is 270 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F43: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G43: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F44: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G44: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F45: Auxiliary power standby draw is 1 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G45: Auxiliary power alarm draw is 125 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F46: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G46: Auxiliary power alarm draw is 140 mA per sounder base. You will need to add this draw to the auxiliary power you are using.

## Smokes
Device Database
Device Database
Command Shortcuts
Item# | Device / Description | Current Draw In Amperes
|  | Standby | *Alarm
1 | Unused
2 | Gentex GCC24 Horn/Strobe (15cd) | 0 | 0.143
3 | Gentex GCC24 Horn/Strobe (30cd) | 0 | 0.153
4 | Gentex GCC24 Horn/Strobe (75cd) | 0 | 0.27
5 | Gentex GCC24 Horn/Strobe (95cd) | 0 | 0.341
6 | Gentex GCC24 Horn/Strobe (115cd) | 0 | 0.383
7 | Gentex GCC24 Horn/Strobe (150cd) | 0 | 0.477
8 | Gentex GCS24 Strobe (15cd) | 0 | 0.12
9 | Gentex GCS24 Strobe (30cd) | 0 | 0.13
10 | Gentex GCS24 Strobe (75cd) | 0 | 0.247
11 | Gentex GCS24 Strobe (95cd) | 0 | 0.318
12 | Gentex GCS24 Strobe (115cd) | 0 | 0.36
13 | Gentex GCS24 Strobe (150cd) | 0 | 0.454
14 | Gentex GEC324 Horn/Strobe (15cd) | 0 | 0.134
15 | Gentex GEC324 Horn/Strobe (30cd) | 0 | 0.152
16 | Gentex GEC324 Horn/Strobe (60cd) | 0 | 0.193
17 | Gentex GEC324 Horn/Strobe (75cd) | 0 | 0.236
18 | Gentex GEC324 Horn/Strobe (110cd) | 0 | 0.28
19 | Gentex GES324 Strobe (15cd) | 0 | 0.078
20 | Gentex GES324 Strobe (30cd) | 0 | 0.096
21 | Gentex GES324 Strobe (60cd) | 0 | 0.137
22 | Gentex GES324 Strobe (75cd) | 0 | 0.18
23 | Gentex GES324 Strobe (110cd) | 0 | 0.224
24 | Gentex GEC24 Horn/Strobe (15cd) | 0 | 0.133
25 | Gentex GEC24 Horn/Strobe (30cd) | 0 | 0.151
26 | Gentex GEC24 Horn/Strobe (60cd) | 0 | 0.192
27 | Gentex GEC24 Horn/Strobe (75cd) | 0 | 0.235
28 | Gentex GEC24 Horn/Strobe (110cd) | 0 | 0.279
29 | Gentex GEC24 Horn/Strobe (177cd) | 0 | 0.343
30 | Gentex GEH24 Horn | 0 | 0.056
31 | Gentex GES24 Strobe (15cd) | 0 | 0.078
32 | Gentex GES24 Strobe (30cd) | 0 | 0.096
33 | Gentex GES24 Strobe (60cd) | 0 | 0.137
34 | Gentex GES24 Strobe (75cd) | 0 | 0.18
35 | Gentex GES24 Strobe (110cd) | 0 | 0.224
36 | Gentex GES24 Strobe (177cd) | 0 | 0.288
37 | Gentex GX91 Mini-Horn (Continuous) | 0 | 0.015
38 | Gentex GX93 Mini-Horn (Temporal) | 0 | 0.022
39 | Gentex WGE Strobe (75cd) | 0 | 0.18
40 | Gentex WGEC Horn/Strobe (75cd) | 0 | 0.236
41 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
42 | System Sensor CH Chime | 0 | 0.054
43 | System Sensor CHS Chime/Stobe (15cd) | 0 | 0.07
44 | System Sensor CHS Chime/Stobe (15/75cd) | 0 | 0.081
45 | System Sensor CHS Chime/Strobe (30cd) | 0 | 0.099
46 | System Sensor CHS Chime/Strobe (75cd) | 0 | 0.165
47 | System Sensor CHS Chime/Strobe (95cd) | 0 | 0.189
48 | System Sensor CHS Chime/Strobe (110cd) | 0 | 0.21
49 | System Sensor CHS Chime/Strobe (115cd) | 0 | 0.217
50 | System Sensor HR/HRK/HW Horn | 0 | 0.069
51 | System Sensor MH Mini-Horn | 0 | 0.029
52 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091
53 | System Sensor P2/PC2 Horn/Strobe (15/75cd) | 0 | 0.1
54 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116
55 | System Sensor P2/PC2 Horn/Strobe (75cd) | 0 | 0.176
56 | System Sensor P2/PC2 Horn/Strobe (95cd) | 0 | 0.201
57 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221
58 | System Sensor P2/PC2 Horn/Strobe (115cd) | 0 | 0.229
59 | System Sensor P2/PC2 Horn/Strobe (135cd) | 0 | 0.255
60 | System Sensor P2/PC2 Horn/Strobe (150cd) | 0 | 0.27
61 | System Sensor P2/PC2 Horn/Strobe (177cd) | 0 | 0.302
62 | System Sensor P2/PC2 Horn/Strobe (185cd) | 0 | 0.309
63 | System Sensor S/SC Strobe (15cd) | 0 | 0.066
64 | System Sensor S/SC Strobe (15/75cd) | 0 | 0.077
65 | System Sensor S/SC Strobe (30cd) | 0 | 0.094
66 | System Sensor S/SC Strobe (75cd) | 0 | 0.158
67 | System Sensor S/SC Strobe (95cd) | 0 | 0.181
68 | System Sensor S/SC Strobe (110cd) | 0 | 0.202
69 | System Sensor S/SC Strobe (115cd) | 0 | 0.21
70 | System Sensor S/SC Strobe (135cd) | 0 | 0.228
71 | System Sensor S/SC Strobe (150cd) | 0 | 0.246
72 | System Sensor S/SC Strobe (177cd) | 0 | 0.281
73 | System Sensor S/SC Strobe (185cd) | 0 | 0.286
74 | System Sensor H-LF Low Freq. Sounder | 0 | 0.153
75 | System Sensor P2H-LF Sounder/Strobe (135cd) | 0 | 0.337
76 | System Sensor P2H-LF Sounder/Strobe (150cd) | 0 | 0.362
77 | System Sensor P2H-LF Sounder/Strobe (177cd) | 0 | 0.387
78 | System Sensor P2H-LF Sounder/Strobe (185cd) | 0 | 0.417
79 | Wheelock AH24 Horn | 0 | 0.08
80 | Wheelock AS241575 Horn/Strobe (1575cd) | 0 | 0.201
81 | Wheelock AS24MCW Horn/Strobe (15cd) | 0 | 0.168
82 | Wheelock AS24MCW Horn/Strobe (30cd) | 0 | 0.205
83 | Wheelock AS24MCW Horn/Strobe (75cd) | 0 | 0.28
84 | Wheelock AS24MCW Horn/Strobe (110cd) | 0 | 0.347
85 | Wheelock AS24MCWH Horn/Strobe (135cd) | 0 | 0.435
86 | Wheelock AS24MCWH Horn/Strobe (185cd) | 0 | 0.56
87 | Wheelock AS24MCC Horn/Strobe (15cd) | 0 | 0.175
88 | Wheelock AS24MCC Horn/Strobe (30cd) | 0 | 0.218
89 | Wheelock AS24MCC Horn/Strobe (75cd) | 0 | 0.301
90 | Wheelock AS24MCC Horn/Strobe (95cd) | 0 | 0.365
91 | Wheelock AS24MCCH Horn/Strobe (115cd) | 0 | 0.435
92 | Wheelock AS24MCCH Horn/Strobe (177cd) | 0 | 0.56
93 | Wheelock CH70 Chime | 0 | 0.022
94 | Wheelock CH70241575 Chime/Strobe (1575cd) | 0 | 0.112
95 | Wheelock CH7024MCW Chime/Strobe (15cd) | 0 | 0.082
96 | Wheelock CH7024MCW Chime/Strobe (30cd) | 0 | 0.114
97 | Wheelock CH7024MCW Chime/Strobe (75cd) | 0 | 0.187
98 | Wheelock CH7024MCW Chime/Strobe (110cd) | 0 | 0.242
99 | Wheelock CH7024MCWH Chime/Strobe (135cd) | 0 | 0.322
100 | Wheelock CH7024MCWH Chime/Strobe (185cd) | 0 | 0.442
101 | Wheelock CH90 Chime | 0 | 0.022
102 | Wheelock CH9024MCC Chime/Strobe (15cd) | 0 | 0.087
103 | Wheelock CH9024MCC Chime/Strobe (30cd) | 0 | 0.127
104 | Wheelock CH9024MCC Chime/Strobe (75cd) | 0 | 0.211
105 | Wheelock CH9024MCC Chime/Strobe (95cd) | 0 | 0.271
106 | Wheelock CH9024MCCH Chime/Strobe (115cd) | 0 | 0.322
107 | Wheelock CH9024MCCH Chime/Strobe (177cd) | 0 | 0.442
108 | Wheelock HS24 Horn | 0 | 0.11
109 | Wheelock HS24MCC Horn/Strobe (15cd) | 0 | 0.175
110 | Wheelock HS24MCC Horn/Strobe (30cd) | 0 | 0.215
111 | Wheelock HS24MCC Horn/Strobe (75cd) | 0 | 0.299
112 | Wheelock HS24MCC Horn/Strobe (95cd) | 0 | 0.359
113 | Wheelock HS24MCCH Horn/Strobe (115cd) | 0 | 0.41
114 | Wheelock HS24MCCH Horn/Strobe (177cd) | 0 | 0.53
115 | Wheelock HS4241575W Horn/Strobe (1575cd) | 0 | 0.2
116 | Wheelock HS424MCW Horn/Strobe (15cd) | 0 | 0.17
117 | Wheelock HS424MCW Horn/Strobe (30cd) | 0 | 0.202
118 | Wheelock HS424MCW Horn/Strobe (75cd) | 0 | 0.275
119 | Wheelock HS424MCW Horn/Strobe (110cd) | 0 | 0.33
120 | Wheelock HS424MCWH Horn/Strobe (135cd) | 0 | 0.41
121 | Wheelock HS424MCWH Horn/Strobe (185cd) | 0 | 0.53
122 | Wheelock MT24 Multitone Appliance | 0 | 0.142
123 | Wheelock MT241575 Multitone/Strobe (1575cd) | 0 | 0.232
124 | Wheelock MTWP2475 Multitone/Strobe (180cd) | 0 | 0.28
125 | Wheelock MT24MCW Multitone/Strobe (15cd) | 0 | 0.202
126 | Wheelock MT24MCW Multitone/Strobe (30cd) | 0 | 0.234
127 | Wheelock MT24MCW Multitone/Strobe (75cd) | 0 | 0.307
128 | Wheelock MT24MCW Multitone/Strobe (110cd) | 0 | 0.362
129 | Wheelock NH24 Horn | 0 | 0.044
130 | Wheelock NS241575W Horn/Strobe (1575cd) | 0 | 0.148
131 | Wheelock NS24MCW Horn/Strobe (15cd) | 0 | 0.118
132 | Wheelock NS24MCW Horn/Strobe (30cd) | 0 | 0.151
133 | Wheelock NS24MCW Horn/Strobe (75cd) | 0 | 0.228
134 | Wheelock NS24MCW Horn/Strobe (110cd) | 0 | 0.288
135 | Wheelock NS24MCC Horn/Strobe (15cd) | 0 | 0.126
136 | Wheelock NS24MCC Horn/Strobe (30cd) | 0 | 0.168
137 | Wheelock NS24MCC Horn/Strobe (75cd) | 0 | 0.253
138 | Wheelock NS24MCC Horn/Strobe (95cd) | 0 | 0.319
139 | Wheelock NS24MCCH Horn/Strobe (115cd) | 0 | 0.394
140 | Wheelock NS24MCCH Horn/Strobe (177cd) | 0 | 0.521
141 | Wheelock RSS/RSSP241575W Strobe (1575cd) | 0 | 0.09
142 | Wheelock RSS/RSSP24MCW Strobe (15cd) | 0 | 0.06
143 | Wheelock RSS/RSSP24MCW Strobe (30cd) | 0 | 0.092
144 | Wheelock RSS/RSSP24MCW Strobe (75cd) | 0 | 0.165
145 | Wheelock RSS/RSSP24MCW Strobe (110cd) | 0 | 0.22
146 | Wheelock RSS/RSSP24MCWH Strobe (135cd) | 0 | 0.3
147 | Wheelock RSS/RSSP24MCWH Strobe (185cd) | 0 | 0.42
148 | Wheelock RSS/RSSP24MCC Strobe (15cd) | 0 | 0.065
149 | Wheelock RSS/RSSP24MCC Strobe (30cd) | 0 | 0.105
150 | Wheelock RSS/RSSP24MCC Strobe (75cd) | 0 | 0.189
151 | Wheelock RSS/RSSP24MCC Strobe (95cd) | 0 | 0.249
152 | Wheelock RSS/RSSP24MCCH Strobe (115cd) | 0 | 0.3
153 | Wheelock RSS/RSSP24MCCH Strobe (177cd) | 0 | 0.42
154 | Silent Knight SK-Control NAC Module | 0.0017 | 0.007
155 | Silent Knight B200S Sounder Base | 0.0005 | 0.035
156 | Silent Knight SK-Zone Two Wire Det Mod | 0.012 | 0.09
157 | Silent Knight B200S-LF Low Freq Sound Base | 0.0005 | 0.14
158 | User Defined
159 | User Defined
160 | User Defined
161 | User Defined
162 | User Defined
163 | User Defined
164 | User Defined
165 | User Defined
166 | User Defined
167 | User Defined
*Alarm draws are listed as worse case. Consult manufacturer's specification sheet for actual alarm draw with the candela and/or horn mode you are using.
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.

## Circuit Config
Circuit Configuration
Project Name: | Portland High School | Project ID: |  | 0 | Alarm Mins:
Prepared By: | Kevin Inman | Date: |  | 2016-06-28 | Voltage Drop Warning Threshold % :
Ckt. Number: | PGM-I/O #1 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
1 | System Sensor S/SC Strobe (15cd) | 0 | 0.066 | 0 | 0.066 | 63
1 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091 | 0 | 0.091 | 52
3 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116 | 0 | 0.348 | 54
2 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221 | 0 | 0.442 | 57
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0.947
Ckt. Number: | PGM-I/O #2 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
6 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091 | 0 | 0.546 | 52
1 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116 | 0 | 0.116 | 54
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0.662
Ckt. Number: | PGM-I/O #3 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
4 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091 | 0 | 0.364 | 52
3 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221 | 0 | 0.663 | 57
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 1.027
Ckt. Number: | PGM-I/O #4 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
1 | System Sensor S/SC Strobe (15cd) | 0 | 0.066 | 0 | 0.066 | 63
4 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091 | 0 | 0.364 | 52
2 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116 | 0 | 0.232 | 54
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0.662
Ckt. Number: | PGM-I/O #5 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #6 | Panel ID: | 5895XL
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0

## Devices (hidden)
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1 | Notification Appl Circuit
2 | Initiating Device Circuit
3 | Aux Power Circuit
| I/O1 | 1
| I/O2 | 1
| I/O3 | 1
| I/O4 | 1
| I/O5 | 1
| I/O6 | 1