## FCPS-24FS6 & 8
Jobsite Information:
FCPS-24FS6 / 8 Battery Calculation
Entries only to be made in the Yellow cell locations
Regulated Load in Standby
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board | 1 | X | 0.065 | = | 0.065
Power Supervision Relays |  | X | 0.025 | = | 0
Auxiliary Current Draw |  | X |  | = | 0
from TB4 Terminals 9 & 10
|  |  | STANDBY LOAD | = | 0.065
Regulated Load in ALARM
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board without AC | 1 | X | 0.145 | = | 0.145
Power Supervision Relays |  | X | 0.025 | = | 0
Auxiliary Current Draw |  | X |  | = | 0
from TB4 Terminals 9 & 10
NAC / Output # 1 | 12 | X | 0.9 | = | 10.8
NAC / Output # 2 | 8 | X | 0.9 | = | 7.2
NAC / Output # 3 | 4 | X | 0.9 | = | 3.6
NAC / Output # 4 |  | X |  | = | 0
|  |  | ALARM LOAD | = | 21.745
Battery Amp Hour Calculation
Standby Load |  |  | Required Standby Time
Current (Amps) |  |  | (Typically 24 or 60 Hours)
| 0.065 | X | 24 | = | 1.56 | AH
Alarm Load |  |  | Required Alarm Time
Current (Amps) |  |  | (Typically 5 or 10 Minutes)
| 21.745 | X | 10 | = | 3.6242 | AH
|  |  |  | Sub Total Standby / Alarm Amp Hours | 5.1842 | AH
|  |  | Multiply by the Derating Factor | X | 1.2 | *
|  |  | Total Ampere Hours Required | = | 6.721 | AH
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.