Submittal

| Prepared For: Brent Grass | Date: February 24, 2017 Customer P.O. Number: Customer Project Number: |
| --- | --- |
| Sold To: HVAC Services | Job Number: Job Name: HVAC Services - Rob - CIEE |

Trane U.S. Inc. dba Trane is pleased to provide the enclosed submittal for your review and approval.

Product Summary

Qty	Product

3	Split System Air Conditioning Units

| Daniel Broderick Trane 860 Spring Street, Unit 1 Westbrook, ME 04092 Phone: (207) 828-1777 Cell: Fax: (207) 828-1511 | The attached information describes the equipment we propose to furnish for this project, and is submitted for your approval. Product performance and submittal data is valid for a period of 6 months from the date of submittal generation. If six months or more has elapsed between submittal generation and equipment release, the product performance and submittal data will need to be verified. It is the customer’s responsibility to obtain such verification. |
| --- | --- |

/tmp/in/input.doc

Table Of Contents

Product Summary	1

Split System Air Conditioning Units (Small) (Items A1, A2)	3

Tag Data	3

Product Data	4

Mechanical Specifications	5

Unit Dimensions	7

Tag Data - Split System Air Conditioning Units (Small) (Qty: 3)

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| A1 | No Tag | 1 | 3 Ton Unitary Split Systems | 4TTA3036B3-----------0-0000000000--------0-TUH1B060A9361-0----0-00000-4TXCB004DS3HC |
| A2 | No Tag | 2 | 5 Ton Unitary Split Systems | 4TTA3060D3-----------0-0000000000--------0-TUH1C080A9601-0----0-00000-4TXCC009DS3HC |

Product Data - Split System Air Conditioning Units (Small)

Item: A1  Qty: 1

Split System Cooling Outdoor Unit

3 Ton Nominal Cooling Capacity

200 - 230 Volt 3 Phase 60 Hertz

Furnace unit	60,000 Heating input BTUH

115 Volt/1 phase/60 hertz

3 Ton Airflow Cooling Capacity

Cased upflow/dnflow/horiz left 	17.5"/16.3"cabinet

36,000 Nominal cooling capacity

Hi efficiency

TXV-Non bleed

Conv-upflow/dnflw,left airflow coil

Item: A2  Qty: 2

Split System Cooling Outdoor Unit

5 Ton Nominal Cooling Capacity

200 - 230 Volt 3 Phase 60 Hertz

Furnace unit	80,000 Heating input BTUH

115 Volt/1 phase/60 hertz

5 Ton Airflow Cooling Capacity

Cased upflow/dnflow/horiz left

21.0"/19.8" cabinet

60,000  Nominal cooling capacity

Hi efficiency

TXV-Non bleed

Conv-upflow/dnflw,left airflow coil

Mechanical Specifications - Split System Air Conditioning Units (Small)

Item: A1, A2   Qty: 3

4TTA3 - General

This unit is fully charged from the factory for matched indoor section and up to 180" of piping.  Unit is designed to operate at outdoor ambient temperatures as high as 115.0 F]. Cooling capacities matched with a wide selection of air handlers and furnace coils that are A.R.I certified.  The unit shall be UL listed.  Exterior must be designed for outdoor application.

4TTA3 - Casing

Unit casing is constructed of heavy gauge, galvanized steel and painted with a weather-resistant powder paint. Corrosion and weatherproof CMBP-G30 Duratuff base.

4TTA3 - Compressor

The Climatuff compressor features internal over temperature and pressure protector, total dipped hermetic motor.  Other features include: centrifugal oil pump, and low vibration and noise.

4TTA3 - Condenser Coil

The Spine Fin coil is continuously wrapped, corrosion resistant, all aluminum with minimum brazed joints.  The coil is 3/8" O.D. seamless aluminum glued to a continuous aluminum fin.  Coils are lab tested to withstand 2000.0 lb of pressure per square inch.  The outdoor coil provides low airflow resistance and efficient heat transfer.

4TTA3 - Refrigerant controls

Refrigeration system controls include condenser fan and compressor contactor.  High and low pressure protection is inherent to the compressor.  Another standard feature is the factory installed liquid line drier.

TUH1 - GENERAL OPERATION

These High Efficiency, Direct Vent, Condensing Gas Furnaces employ a Hot Surface Ignition system, which eliminates the waste of a constantly burning pilot. They are convertible for HORIZONTAL use by rotating the unit to its left side. The integrated system control lights the main burners upon a demand for heat from the room thermostat. Complete front service

access.

a. Low energy power venter.

b. Vent proving differential switch.

TUH1 - NATURAL GAS MODELS

Central heating furnace designs are certified by the American Gas Association for both natural and L.P. gas. Limit setting and rating data were established and approved under standard rating conditions using American National Standards Institute standards.

TUH1 - SAFE OPERATION

The Integrated System Control has solid state devices, which continuously monitor for presence of flame, when the system is in the heating mode of operation. Slow opening, dual solenoid combination gas valve and regulator provide extra safety and quieter operation.

TUH1 - QUICK HEATING

Durable, cycle tested, heavy gauge aluminized steel heat exchanger and stainless steel secondary heat exchanger quickly transfer over 90% of the heat to provide warm conditioned air to the structure. Low energy power vent blower, to increase efficiency and provide a positive discharge of gas fumes to the outside as it draws outdoor air in for sealed combustion, which means it uses no indoor air for combustion.

TUH1 - BURNERS

Multi-port, in-shot burners will give years of quiet and efficient service. All models can be converted to L.P. gas without changing burners.

TUH1 - INTEGRATED SYSTEM CONTROL

Exclusively designed operational program provides total control of furnace limit sensors, blowers, gas valve, flame control and includes self diagnostics for ease of service. The built-in, selectable "Cooling Fan Off" feature provides time-delay capability like a BAY24X045 Time-Delay Kit for cooling operation. Also contains connection points for E.A.C./humidifier.

TUH1 - AIR DELIVERY

The multispeed, directdrive blower motor, with sufficient airflow range for most heating and cooling requirements, will switch from heating to cooling speeds on demand from room

thermostat. The blower door safety switch will prevent or terminate furnace operation when the blower door is removed. (Fan relay and 35VA control transformer is standard).

TUH1 - STYLING

Heavy gauge steel and "wraparound" cabinet construction is used in the cabinet with baked-on enamel finish for strength and beauty. The heat exchanger section of the cabinet is completely lined with foil-faced fiberglass insulation. This results in quiet and efficient operation due to the excellent acoustical and insulating qualities of fiberglass.

4TXC - General

Upflow, Downflow, or Horizontal coils shall be designed for cooling and heat pump applications. The coil shall be 3/8" seamless aluminum tubing mechanically bonded to aluminum plate fin.

Refrigerant for the TXC coils shall be controlled with factory installed Non-Bleed TXV refrigerant control. Refrigerant connections are brazed fittings with an additional Schrader Valve for system service.

The coil cabinet shall have a removable front and interior access panel for evaporator coil entering air surface cleaning.

The coil includes a drain pan with drain connections for vertical or horizontal operation and a horizontal auxiliary drain pan.

These coils are A.R.I. certified with Trane's matching condensing units.

4TXC - Accessories

Evaporator Defrost Control installed on coil for lower ambient operating conditions.

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A1   Qty: 1

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A1   Qty: 1

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A1   Qty: 1

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A1   Qty: 1

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A1   Qty: 1

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A2   Qty: 2

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A2   Qty: 2

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A2   Qty: 2

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A2   Qty: 2

Unit Dimensions - Split System Air Conditioning Units (Small)

Item: A2   Qty: 2