From: 	Chris Pirone
To:	Jean Fraser
Date: 	6/7/2012 12:23 PM
Subject: 	Comments

Fire Comments:
 
All construction shall comply with City Code Chapter 10.
http://www.portlandmaine.gov/citycode/chapter010.pdf
 
If the building has a sprinkler system; fire hydrants must be within 100’ but no closer than 40’.
 
Fire Department Connections shall not be located where large diameter hose may block egress.

Street addresses shall be marked on the structure and shall be as approved by the City E-911 Addressing Officer.  Contact Michelle Sweeney at 874-8682 for further information. 
 
Note*Pay special attention to code requirements reference carbon monoxide protection since there is parking in the structure.

 
Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410