John Meehan (603)926-9401

Need to call Captiveaire to determine if the equipment is listed for the purpose: venting wood smoke and grease-laden vapors.

A stamped letter from the PE that designed the oven stating the minimum design requirements for such an oven as determined by NFPA 96-2008 edition and NFPA 211-2006 edition, and that it meets or exceeds each individual requirement. Based upon that letter, and following completion a stamped compliance letter for the same, a cross sections of the unit will not need to be submitted. We will also require a compliance letter for the entire completed installation (NFPA 96 and 211).

Front and rear elevations of the installation showing the oven, hood, duct work, exhaust fan assembly, and vent termination and their relation to each other and combustible or limited combustible materials. The relation of the oven openings and hood are paramount as is the exhaust termination.

96:14.4.4 prohibits wall terminations and has since at least 1998. A roof top termination in accordance with 96:7.8.2 will be required.

96:14.1.3 and 96:14.6.3 requires makeup air interlocked with the exhaust system.

A separate suppression system permit will be required. 96:14.7.5 requires the suppression system to be water-based.