Inspection Services                                       		Department of Urban Development

Michael J. Nugent			                                                  Joseph E. Gray, Jr.

Manager                                                                                                                                Director

CITY OF PORTLAND

Joseph Soley										July 26, 1999

Monopoly Inc.

P. O. Box 367 DTS

Portland, Maine 04226-0367

RE:  9-11 Exchange Street

CBL:  032-F-010

Dear Mr. Soley,

A recent inspection conducted on or about June 23, 1999, revealed the following electrical

violations and unsafe conditions, which shall be corrected, pursuant to ZNEC 1999 and all applicable electrical codes.

APARTMENT #2A:

---No violations.

APARTMENT #2C:

---Provide GFCI protection at the kitchen counter.

---Electrical panel is now blocked.  Maintain a 36” clearance at all times.

STORAGE CLOSET SECOND FLOOR:

---Install proper signage on the entry door, which shall read:   “DANGER, ELECTRICAL ROOM, AUTHORIZED PERSONELL ONLY.”

APARTMENT #2B:

---Provide GFCI protection at the kitchen counter.

APARTMENT #2E:

---Missing fixture glob in the bathroom.

---Extension cord is being used as a clothesline.

APARTMENT #3B:

---Provide GFCI protection at the kitchen counter.

APARTMENT #3D:

---Provide GFCI protection at the kitchen counter.

APARTMENT #3E:

---No entry.

APARTMENT #3A:

---No entry.

APARTMENT #3G:

---No entry.

APARTMENT #3F:

---No entry.

APARTMENT #4:

---Provide GFCI protection at the kitchen counter.

These electrical violations and unsafe conditions shall be corrected no later than August 13,

- Failure to comply shall result in further legal action to be taken by this office.

Sincerely,

Michael A. Collins, Chief Electrical Inspector

City of Portland

Cc:  Mike Nugent, ISM

- Rowe, CEO

D. Caddell, CEO

Lt. McDougall, PFD

Charlie Lane, Corp Counsel