Inspection Services                                       		Department of Urban Development

Michael J. Nugent			                                                  Joseph E. Gray, Jr.

Manager                                                                                                                                Director

CITY OF PORTLAND

# Joseph Soley/Steve Bauman								            12/14/2000

1 Exchange Street

Portland, Maine 04101

CBL:  032-f-014

Dear Sir(s);

An electrical inspection was conducted at the above address on 12/13/00.  The following violations and unsafe conditions were revealed and shall be corrected, per NEC 1999 and all applicable codes.

- Boiler/sprinkler room:

---(3) Missing relay covers

- General bar areas:

---Broken device plates

---Broken devices, i.e. (switches, receptacles)

---KO seals missing at junction boxes

---Secure low-voltage wiring, throughout

---Add exit sign per PFD

- Beer cooler:

---Improper wiring of evaporator and fan

---Add wall switch for interior light

---Globe and cage missing at light fixture

---KO seals missing at junction boxes

- Electrical room/Milk Street:

---Add wall switch for light

---This room shall have no storage

These violations and unsafe conditions shall be corrected and a re-inspection conducted prior to occupancy of this retail space.

Sincerely,

Michael A. Collins, Chief Electrical Inspector

Cc:  Central file, A. Rowe, Lt. McDougall