Inspection Services                                       		Department of Urban Development

Michael J. Nugent			                                                  Joseph E. Gray, Jr.

Manager                                                                                                                                Director

CITY OF PORTLAND

# Joseph Soley										July 26, 1999

Monopoly Inc.

P. O. Box 367 DTS

Portland, Maine 04226-0367

RE:  8-10 Exchange Street

CBL:  032-I-012

Dear Mr. Soley,

A recent inspection conducted on or about June 23, 1999, revealed the following electrical

violations and unsafe conditions, which shall be corrected, pursuant to NEC 1996 and all applicable electrical codes.

APARTMENT #402:

---No violations found.

APARTMENT #401:

---Extension cord passing through a wall under the stairs.

APARTMENT #404:

---Cover plate missing.

---Recessed light trim missing in bathroom.

---Add GFCI protection in the bathroom.

STORAGE AREA 4th FLOOR:

---Remove ZIP cord and illegal fixtures.  Install approved lighting in this area.

APARTMENT #405:

---Loose range receptacle.

---Cover plates missing.

---Loose ceiling fixture.

APARTMENT #407:

---Repair or replace noisy bath exhaust fan.

---Properly adjust electrical panel interior.

APARTMENT #408:

---Loose receptacle at kitchen counter.

APARTMENT #406:

---Bathroom GFCI receptacle is not working properly.

APARTMENT #409:

---No entry

APARTMENT #410:

---Smoke detector missing.

---Remove extension cords.  Add receptacles as needed.

---Install GFCI protection in the bathroom.

---Replace broken wall switch.

APARTMENT #412:

---Loose circuit breaker in electrical panel.

---Remove extension cords.  Add receptacles as needed.

APARTMENT #414:

---Vacant, no power.

---Loose Armored Cables, type AC near entry to apartment.

---Provide GFCI protection at kitchen counter.

APARTMENT #413:

---Smoke detector missing.

---Provide GFCI protection at the kitchen counter.

APARTMENT #411:

---No entry.

APARTMENT #311:

---Provide GFCI protection at the kitchen counter.

APARTMENT #306:

---Provide GFCI protection at the kitchen counter.

APARTMENT #313:

---Missing receptacle plate in the kitchen.

---Re-secure the EMT conduit, which feeds the smoke detector.

---Install a new lens for the bathroom shower fixture.

APARTMENT #312:

---Smoke detector missing.

---Label electrical panel.

---Provide GFCI protection for the bathroom and at the kitchen counter.

---Fixture missing on the ceiling in the kitchen area.

APARTMENT #314:

---Provide GFCI protection at the kitchen counter.

---Bathroom receptacle is loose.

---Label panel.

APARTMENT #310:

---Loose, exposed wiring at water heater.

---Missing wall plates.

APARTMENT #309:

---No entry.

APARTMENT #308:

---No entry.

APARTMENT #307:

---Blank off or provide GFCI protection for bathroom receptacle.

---Loose wall receptacle.

---Re-secure range receptacle.

---Label electrical panel.

APARTMENT #305:

---Relocate receptacles over the range.

---Repair or replace bathroom GFCI receptacle.

---Missing smoke detector.

APARTMENT #303:

---Provide GFCI protection at the kitchen counter.

---Label electrical panel.

APARTMENT #304:

---No entry.

APARTMENT #301:

---Missing wall plates.

---Label electrical panel.

APARTMENT #302:

---No entry.

These electrical violations and unsafe conditions shall be corrected no later than August 13, 1999.  Failure to comply shall result in further legal action to be taken by this office.

Sincerely,

Michael A. Collins, Chief Electrical Inspector

City of Portland

Cc:  Mike Nugent, ISM

- Rowe, CEO

D. Caddell, CEO

Lt. McDougall, PFD; Charlie Lane, Corp Counsel