From: 	Marge Schmuckal
To:	Helen Donaldson
Date: 	3/19/2014 4:02 PM
Subject: 	Hotel dBAs

Hi Nell,
What I received shows different information. Greg Staed that the C-=Gen decibel rating is 54-56 which meets the B-3 external effects. However, the rest of what he sent shows perhaps other equipment that list overall dBAs of 67, 63, 68, & 62.  the B-3 maximizes 60 during day time and 55 during night time.  That could be alright if the readings were done right at the unit. The readings may be different at the property lines.  I would need that to be explained.
 
I don't think I got a permit for these units yet. They would be required to get separate permits for these units.
 
Marge