Public Services Department

Michael J. Bobinsky, Director

## 1 November 2012

Ms. Denise Cameron, P.E.,

Woodard & Curran,

41 Hutchins Drive,

Portland, Maine 04102

# RE: The Capacity to Handle Wastewater Flows, from the

# Proposed Canal Plaza Hotel, at 433 Fore Street.

Dear Ms. Cameron:

The existing fifteen-inch diameter, vitrified clay sanitary sewer pipe, located in Fore Street, has adequate capacity to transport, while The Portland Water District sewage treatment facility, located off Marginal Way, has adequate capacity to treat, the total anticipated increase in wastewater flows of 13,935 GPD, from this development.

The City combined sewer overflow (C.S.O.) abatement consent agreement (with the U.S.E.P.A., and with the Maine D.E.P.) requires C.S.O. abatement, as well as storm water mitigation, in order to offset any increase in sanitary flows, from all projects.

If the City can be of further assistance, please call 874-8832.

Sincerely,

CITY OF PORTLAND

Frank J Brancely, B.A., M.A.

Senior Engineering Technician

FJB

CC:        Barbara Barhydt, Development Review Services Manager, Department of Planning, and Urban Development, City of Portland

Helen Donaldson, Planner, Department of Planning, and Urban Development, City of Portland

David Margolis-Pineo, Deputy City Engineer, City of Portland

Michael Farmer, P.E., Project Engineer, City of Portland

Bradley A. Roland, P.E., Environmental Projects Engineer, City of Portland

Stephen K. Harris, Assistant Engineer, City of Portland

John Emerson, Wastewater Coordinator, City of Portland

Rhonda Zazzara, Field Inspection Coordinator, City of Portland

Jane Ward, Administrative Assistant, City of Portland

Ms. Megan LaPierre McDevitt, P.E.,

Woodard & Curran,

October 10, 2012,

Page 2.

Anticipated Wastewater Flows from the Proposed Hotel:

The Proposed Restaurant:

36 Proposed Two-Meal Restaurant Seats @ 30 GPD/Seat		    =        1,080 GPD

5 Proposed Employees @ 15 GPD/Employee			                 =             75 GPD

The Proposed Hotel:

123 Proposed Hotel Rooms @ 100 GPD/Hotel Room                                    =       12,300 GPD

29 Proposed Employees @ 15 gpd per Employee			    =            435 GPD

The Proposed Retail Spaces:

3 Proposed Employees @ 15 GPD/Employee			                 =               45 GPD

Total Proposed Increase in Wastewater Design Flows for this Project     =        13,935 GPD