From: 	David Margolis-Pineo
To:	Barbara Barhydt;  Helen Donaldson
CC:	Kevin Noyes;  Michael Farmer
Date: 	5/7/2015 12:17 PM
Subject: 	Condition of Approval Comments for 195 Anderson St

Nell,
 
Please submit the comments below to the applicant.  Thanks
 
I'll also place in Urban Insight.

May 7, 2015
 
Memo To:        Nell Donaldson
                        Michael Farmer
                        Barbara Barhydt
From:               David Margolis-Pineo
Re:                   195 Kennebec Street – Century Tire (2015-027)
 
The Department of Public Services has the following comments addressing the proposed street lighting for this project as shown on Plan E1.00 Revised on May 1, 2015.
 
1.      On Marginal Way, where does the proposed electrical conduit connect to the existing lighting circuit?  Show the location and details of the connection.  Show the location of the conduit to be installed.
2.      On Kennebec Street, show connection from the proposed meter to  the utility power grid.  Show the electrical panel design details.
3.      Specify the conduit size, type, and provide installation detail showing the depth of cover (minimum of 36”), conduit encasement, and marker tape.
4.      Specify and show the conduit location with respect to right of way or some other reference.
5.      Are light fixtures, poles, and pole foundations details provided?
6.      The applicant will be responsible for all connections, wiring and any other ancillary work required for a complete street project.  Please delete reference that the City is responsible for such work.
7.      It is understood that all street lighting will have LED fixtures, all circuits metered for City billing and please not that a 120v outlet per pole is not required.
 
This Department has no further comments.