Inspection Services                                       		Department of Urban Development

Michael J. Nugent			                                                  Joseph E. Gray, Jr.

Manager                                                                                                                                Director

CITY OF PORTLAND

Bubba Larkin											February 3, 2000

Bubba’s Cafe

92 Portland Street

Portland, Maine 04101

CBL:

RE:  Electrical violations

Recent inspections conducted on 10/267/99 and again on 02/03/00, revealed the following violations and unsafe conditions, which present a clear and present danger to the building and its occupants, creating severe fire and safety hazards, shall be corrected.

----Remove all extension cords above the suspended ceilings and install proper wiring methods to serve all equipment as needed.

----The illegal wiring in the kitchen addition shall be removed and reinstalled by a Maine licensed electrical contractor.

----Relocate the water heater, which is in violation of the required working clearances for electrical equipment.

----Open junction boxes, throughout ceilings and bar room areas.

----Open wiring throughout ceilings and bar room areas.

----Open splices throughout ceilings and bar room areas.

----The main electrical room shall be kept clean and free from all storage items.

----Broken switches and receptacles.

----Outside signage and lighting shall be brought up to code compliance with approved methods.