Inspection Services                                       		Department of Urban Development

Michael J. Nugent			                                                  Joseph E. Gray, Jr.

Manager                                                                                                                                Director

# CITY OF PORTLAND

Mike Scarks											                 05/15/2001

Neptune Properties

120 Exchange Street

Portland, Maine 04101

RE:  340 Cumberland Ave.

CBL:  037 f009

Certified Mail # 7099340000195716 1097

Dear Mr. Scarks,

I have recently received the stamped/engineered electrical drawings, stamped by Harold Thomas, from Mancini Electric for the Internet Hotel @ 340 Cumberland Avenue.

The drawings have been reviewed by myself and have met with my approval.  The drawings do not reflect the existing 600amp, 3 phase 120-208volt service.  Only one service is allowed to serve this building.  The existing service is hereby condemned due to its unsafe condition.

Therefore the existing service shall de-energized and eliminated, in order to facilitate the installation of the new 3000amp, 3 phase 277-480 volt service, pursuant to the following articles of the 1999 NEC.

ARTICLE 90-1: Practical safeguarding

ARTICLE 90-4: Enforcement

ARTICLE 110-11: Deteriorating Agents

ARTICLE 230-2: Number of Services

The new service entrance shall not become energized until the existing service entrance has been eliminated.  Please feel free to contact me if you have any further questions concerning this matter.

Sincerely,

Michael A. Collins

Chief Electrical Inspector

City of Portland