Heating Coil (HTCL)

Job Information

MECA 2008

Comments

Model number

D--B18

Coil Information

Steam Information

Stacked Information

Hot Water Information

Note:  Rated and Certified in accordance with the current edition of ARI Standard 410.

Tag

AC-1

Quantity

1

System type

Hot Water

Unit size

Coil type

TT

Coil tube drainability

Not drainable

Rows

2

Nominal coil height

18"  (457 mm)

Finned length

60" (1524 mm)

Fin type

Prima-Flo E

Tube matl/wall thickness

.020 (0.508 mm)  copper

Fin spacing

110 fins per foot

Fin material

Aluminum

Coil coating

No

Turbulators

No

Actual airflow

2571 cfm

Entering dry bulb

45.00 F

Leaving dry bulb

93.49 F

Total capacity

135.23 MBh

Actual coil face area

7.50 sq ft

APD

0.08 in H2O

Volume

1.93 gal

Elevation

0.00 ft

Max face velocity

Face velocity

343 ft/min

Max air PD

Max fin spacing

Rigging weight

70.0 lb

Installed weight

86.0 lb

Fluid type

Water

Fluid concentration

Standard fluid flow rate

3.00 gpm

Entering fluid temp

180.00 F

Fluid temp drop

90.30 F

Leaving fluid temp

89.70 F

Fluid PD

4.56 ft H2O

Fluid velocity

1.93 ft/sec

Max fluid PD

Fouling factor

0.00050 hr-sq ft-deg F/Btu

Modulated

Degrees superheat

Condensate flow rate

Steam PD

Steam pressure

Qty of stacked coil #1

Qty of stacked coil #2

Qty of stacked coil #3

1.00 Each

1.00 Each

Nominal ht stacked coil #1

18

Nominal ht stacked coil #2

24

Nominal ht stacked coil #3

Coil bank airflow

6000 cfm

Coil bank total cap

315.53 MBh

Coil bank standard flow rate

7.00 gpm

Coil bank fluid PD

4.56 ft H2O

Coil bank installed weight

200.8 lb

Coil bank rigging weight

163.3 lb

Coil bank volume

4.50 gal

Reynolds number

19276.55 Each

3/31/2008

Product Version

1.2

N:\2800 to 2899 Jobs\2806 MECA 2008\Calculations\2806.psd

Heating Coil (HTCL)

Job Information

MECA 2008

Comments

Model number

D--B24

Coil Information

Steam Information

Stacked Information

Hot Water Information

Note:  Rated and Certified in accordance with the current edition of ARI Standard 410.

Tag

AC-1

Quantity

1

System type

Hot Water

Unit size

Coil type

TT

Coil tube drainability

Not drainable

Rows

2

Nominal coil height

24"  (610 mm)

Finned length

60" (1524 mm)

Fin type

Prima-Flo E

Tube matl/wall thickness

.020 (0.508 mm)  copper

Fin spacing

110 fins per foot

Fin material

Aluminum

Coil coating

No

Turbulators

No

Actual airflow

3429 cfm

Entering dry bulb

45.00 F

Leaving dry bulb

93.49 F

Total capacity

180.31 MBh

Actual coil face area

10.00 sq ft

APD

0.08 in H2O

Volume

2.57 gal

Elevation

0.00 ft

Max face velocity

Face velocity

343 ft/min

Max air PD

Max fin spacing

Rigging weight

93.3 lb

Installed weight

114.7 lb

Fluid type

Water

Fluid concentration

Standard fluid flow rate

4.00 gpm

Entering fluid temp

180.00 F

Fluid temp drop

90.30 F

Leaving fluid temp

89.70 F

Fluid PD

4.56 ft H2O

Fluid velocity

1.93 ft/sec

Max fluid PD

Fouling factor

0.00050 hr-sq ft-deg F/Btu

Modulated

Degrees superheat

Condensate flow rate

Steam PD

Steam pressure

Qty of stacked coil #1

Qty of stacked coil #2

Qty of stacked coil #3

1.00 Each

1.00 Each

Nominal ht stacked coil #1

18

Nominal ht stacked coil #2

24

Nominal ht stacked coil #3

Coil bank airflow

6000 cfm

Coil bank total cap

315.53 MBh

Coil bank standard flow rate

7.00 gpm

Coil bank fluid PD

4.56 ft H2O

Coil bank installed weight

200.8 lb

Coil bank rigging weight

163.3 lb

Coil bank volume

4.50 gal

Reynolds number

19276.55 Each

3/31/2008

Product Version

1.2

N:\2800 to 2899 Jobs\2806 MECA 2008\Calculations\2806.psd

Heating Coil (HTCL)

Job Information

MECA 2008

Comments

Model number

D--B33

Coil Information

Steam Information

Stacked Information

Hot Water Information

Note:  Rated and Certified in accordance with the current edition of ARI Standard 410.

Tag

AC-2

Quantity

1

System type

Hot Water

Unit size

Coil type

TT

Coil tube drainability

Not drainable

Rows

2

Nominal coil height

33"  (838 mm)

Finned length

46" (1168 mm)

Fin type

Prima-Flo E

Tube matl/wall thickness

.020 (0.508 mm)  copper

Fin spacing

87 fins per foot

Fin material

Aluminum

Coil coating

No

Turbulators

No

Actual airflow

4000 cfm

Entering dry bulb

45.00 F

Leaving dry bulb

90.00 F

Total capacity

195.21 MBh

Actual coil face area

10.54 sq ft

APD

0.08 in H2O

Volume

2.76 gal

Elevation

0.00 ft

Max face velocity

Face velocity

379 ft/min

Max air PD

Max fin spacing

Rigging weight

86.0 lb

Installed weight

109.0 lb

Fluid type

Water

Fluid concentration

Standard fluid flow rate

5.00 gpm

Entering fluid temp

180.00 F

Fluid temp drop

78.18 F

Leaving fluid temp

101.82 F

Fluid PD

7.63 ft H2O

Fluid velocity

2.76 ft/sec

Max fluid PD

Fouling factor

0.00050 hr-sq ft-deg F/Btu

Modulated

Degrees superheat

Condensate flow rate

Steam PD

Steam pressure

Qty of stacked coil #1

Qty of stacked coil #2

Qty of stacked coil #3

Nominal ht stacked coil #1

Nominal ht stacked coil #2

Nominal ht stacked coil #3

Coil bank airflow

Coil bank total cap

Coil bank standard flow rate

Coil bank fluid PD

Coil bank installed weight

Coil bank rigging weight

Coil bank volume

Reynolds number

28964.13 Each

3/31/2008

Product Version

1.2

N:\2800 to 2899 Jobs\2806 MECA 2008\Calculations\2806.psd