| Business Name/Owner/Mgr/Location | Inspector | CAPT D. JACKSON |  | Inspection Date |
| --- | --- | --- | --- | --- |
| 494-498 CONGRESS STREET |  | BENJAMIN WALLACE JR |  | 8/18/2009 |  |
| PAUL SMITH |  |  |  |  |  |  |
| PO Box 1300 | Building Number | CBL | Inspection Type |  |
| Manchester, NH | 681 |  | 037 I001001 | ROUTINE INSPECTION |

- Structure requires a complete automatic fire alarm system through out with central station monitoring.

- The stairs at 496 Congress St. require one-hour fire door assemblies.

- Tenant doors are not identified at 496 Congress Street (Suite #s).

- Emergency lighting is non-functional.

- Basement access door to be labeled.

- Produce sprinkler test report and statement of code compliance.

- Sprinkler system does not have alarm or fire department connection, and is not supervised by a fire alarm system.  Suspended ceiling blocks sprinkler heads at 494 Congress Street.

- Numerous out of service systems in basement and above ceiling at 494 Congress Street.  Such systems shall not be abandoned in place.

- Basement ceiling to be smoke tight.  Basement door to be self-closing and smoke tight.

- A Fire Department Knox Box is required for buildings with fire alarm systems.

- Ceiling tiles missing at 498 Congress Street.  Ceiling must be smoke tight.

- Illegal lock on exit at 498 Congress Street.

- Outlet covers missing at 498 Congress Street.

- Rear door at 498 Congress Street marked as exit has illegal locking hardware.  This door is not a required exit.