SECTION 10520

FIRE-PROTECTION SPECIALTIES

PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary

Conditions and DIVISION 1 Specification Sections, apply to this Section.

1.02	SUMMARY

A.	This Section includes the following:

1.	Portable fire extinguishers.

2.	Fire-protection cabinets for portable fire extinguishers.

B.	Related Sections include the following:

1.	DIVISION 7 Section "Through-Penetration Firestop Systems" for firestopping sealants at 	fire-rated cabinets.

2.	DIVISION 9 painting Sections for field painting fire-protection cabinets.

1.03	SUBMITTALS

A.	General:  Submit in accordance with Section 01330.

B.	Product Data:  Include construction details, material descriptions, dimensions of 	individual 	components and profiles, and finishes for fire-protection cabinets.

1.	Fire Extinguishers:  Include rating and classification.

2.	Fire-Protection Cabinets:  Include roughing-in dimensions, details showing 	mounting 	methods, relationships of box and trim to surrounding construction, door 	hardware, and 	cabinet	 type, trim style, and panel style.

C.	Maintenance Data:  For fire extinguishers and fire-protection cabinets to include in 	maintenance 	manuals.

1.04	QUALITY ASSURANCE

A.	Source Limitations:  Obtain fire extinguishers and fire-protection cabinets through one 	source 	from a single manufacturer.

B.	NFPA Compliance:  Fabricate and label fire extinguishers to comply with NFPA 10, 	"Portable 	Fire Extinguishers."

C.	Fire Extinguishers:  Listed and labeled for type, rating, and classification by an 	independent 	testing agency acceptable to authorities having jurisdiction.

1.	Provide fire extinguishers approved, listed, and labeled by FMG.

D.	Fire-Rated Fire-Protection Cabinets:  Listed and labeled to comply with requirements of

ASTM E 814 for fire-resistance rating of walls where they are installed.

1.05	COORDINATION

A.	Coordinate size of fire-protection cabinets to ensure that type and capacity of fire 	extinguishers 	indicated are accommodated.

1.06	SEQUENCING

A.    Apply vinyl lettering on field-painted fire-protection cabinets after painting is complete.

PART 2 - PRODUCTS

2.01	MATERIALS

A.	Cold-Rolled Steel Sheet:  ASTM A 1008/A 1008M, Commercial Steel (CS), Type B.

B.	Aluminum:  Alloy and temper recommended by aluminum producer and manufacturer for 	type of 	use and finish indicated, and as follows:

1.	Sheet:  ASTM B 209.

2.	Extruded Shapes:  ASTM B 221.

C.	Tempered Float Glass:  ASTM C 1048, Kind FT, Condition A, Type I, Quality q3, 3 mm 	thick, 	Class 1 (clear).

2.02	PORTABLE FIRE EXTINGUISHERS

A.	Manufacturers:

1.	Amerex Corporation.

2.	JL Industries, Inc.

3.	Larsen's Manufacturing Company.

4.	Potter Roemer; Div. of Smith Industries, Inc.

B.	General:  Provide fire extinguishers of type, size, and capacity for each fire-protection 	cabinet and 	mounting bracket indicated.

C.	Multipurpose Dry-Chemical Type in Steel Container:  UL-rated, with mono ammonium

phosphate-based dry chemical in enameled-steel container in the following nominal 							capacities:

1.	Provide -A: 60-B: C, 10-lb

2.03	FIRE-PROTECTION CABINET

A.	Products:

1.	JL Industries, Inc.; Ambassador Series.

2.	Larsen's Manufacturing Company; Architectural Series.

3.	Potter Roemer; Div. of Smith Industries, Inc.; Alta Series.

B.	Cabinet Type:  Suitable for fire extinguisher.

C.	Cabinet Construction:  Non-rated and 1-hour rated as required for wall construction where cabinet 	is located.

D.	Cabinet Material:  Enameled-steel sheet.

1.	Shelf:  Same metal and finish as cabinet.

E.	Semi recessed Cabinet:  Cabinet box partially recessed in walls of shallow depth to suit 	style of 	trim indicated; with one-piece combination trim and perimeter door frame 	overlapping 	surrounding wall surface with exposed trim face and wall return at outer edge 	(backbend).

1.	Rolled-Edge Trim:   2-1/2-inch backbend depth.

F.	Cabinet Trim Material:  Steel sheet.

G.	Door Material:  Steel sheet.

H.	Door Style:  Vertical duo panel with frame.

I.	Door Glazing:  Tempered float glass (clear).

J.	Door Hardware:   Manufacturer's standard door-operating hardware of proper type for 	cabinet 	type, trim style, and door material and style indicated.

1.	Provide manufacturer's standard.

K.	Accessories:

1.	Mounting Bracket:  Manufacturer's standard steel, designed to secure fire 	extinguisher to 	fire-protection cabinet, of sizes required for types and capacities of 	fire extinguishers 	indicated, with plated or baked-enamel finish.

L.	Finishes:

1.	Steel:  Factory primed for field painting.

2.04	FABRICATION

A.	Fire-Protection Cabinets:  Provide manufacturer's standard box (tub), with trim, frame, 	door, and 	hardware to suit cabinet type, trim style, and door style indicated.

1.	Weld joints and grind smooth.

2.	Construct fire-rated cabinets with double walls fabricated from 0.0428-inch thick, cold-	rolled steel sheet lined with minimum 5/8-inch- thick, fire-barrier material.

a.	Provide factory-drilled mounting holes.

B.	Cabinet Doors:  Fabricate doors according to manufacturer's standards, from materials 	indicated 	and coordinated with cabinet types and trim styles selected.

1.	Fabricate doorframes with tubular stiles and rails and hollow-metal design, 	minimum

½-	inch thick.

2.	Miter and weld perimeter door frames.

C.	Cabinet Trim:  Fabricate cabinet trim in one piece with corners mitered, welded, and 	ground 	smooth.

2.05	FINISHES, GENERAL

A.	Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" 	for 	recommendations for applying and designating finishes.

B.	Protect mechanical finishes on exposed surfaces from damage by applying a strippable,

temporary protective covering before shipping.

C.	Finish fire-protection cabinets after assembly.

2.06	STEEL FINISHES

A.	Surface Preparation:  Clean surfaces of dirt, oil, grease, mill scale, rust, and other contaminants 	that could impair paint bond using manufacturer's standard methods.

B.	Factory Priming for Field-Painted Finish:  Apply shop primer specified below immediately after

surface preparation and pretreatment.

1. 	Shop Primer:  Manufacturer's or fabricator's standard, fast-curing, lead- and chromate-

free, universal primer, selected for resistance to normal atmospheric corrosion, for 
		compatibility with substrate and field-applied finish paint system indicated, and for 
		capability to provide a sound foundation for field-applied topcoats despite prolonged 
		exposure.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Examine walls and partitions for suitable framing depth and blocking where semi recessed

cabinets will be installed.

B.	Examine fire extinguishers for proper charging and tagging.

1.	Remove and replace damaged, defective, or undercharged units.

3.02	PREPARATION

A.	Prepare recesses for semi recessed fire-protection cabinets as required by type and size of

cabinet and trim style.

3.03	INSTALLATION

A.	General:  Install fire-protection specialties in locations and at mounting heights indicated or, if

not indicated, at heights indicated below:

1.	Fire-Protection Cabinets: 54-inches above finished floor to top of cabinet.

B.	Fire-Protection Cabinets:  Fasten fire-protection cabinets to structure, square and plumb.

1.	Fasten mounting brackets to inside surface of fire-protection cabinets, square and plumb.

C.	Mounting Brackets:  Fasten mounting brackets to surfaces, square and plumb, at locations

indicated, or if not indicated, as directed by Architect.

D.	Identification:  Apply vinyl lettering for wall-mounted fire extinguishers at locations indicated.

3.04	ADJUSTING AND CLEANING

A.	Remove temporary protective coverings and strippable films, if any, as fire-protection

specialties are installed, unless otherwise indicated in manufacturer's written installation

instructions.

B.	Adjust fire-protection cabinet doors to operate easily without binding.  Verify that integral

locking devices operate properly.

C.	On completion of fire-protection cabinet installation, clean interior and exterior surfaces as

recommended by manufacturer.

D.	Replace fire-protection cabinets that have been damaged or have deteriorated beyond successful

repair by finish touchup or similar minor repair procedures.

END OF SECTION 10520