FIRESTOPPING & SMOKE SEALS

SECTION 07860

1                  General

1.1              SECTION INCLUDES

.1         Comply with Division 1, General Requirements and Documents referred to therein.

.2          It is the intent of this section of the specifications to establish a single, competent 
                    source to be responsible for providing all labour, materials, products, equipment 
                    and services, to supply and install the firestopping and smoke seal work for the 
                    entire project, at the following locations:

Openings in fire rated walls, floors and roofs both empty and those containing penetrations such as cables, conduits, cable pipes, ducts and similar penetrating items.

Gaps between fire-rated walls and exterior walls.

Openings at each floor level in fire rated shafts or stairwells.

Gaps between the tops of fire rated walls and underside of fire rated floor or roof assemblies.

Penetrations through smoke barriers and construction enclosing compartmentalized areas involving both empty openings and openings containing penetrating items.

1.2             RELATED WORK SPECIFIED ELSEWHERE

.1        Openings through Floors and Walls:

Fire Rated: Metal sleeves for fire rated openings through floors and walls shall be provided under applicable mechanical and electrical specification sections.

Non-Rated: Non-rated openings through floors and walls shall be sealed under applicable mechanical and electrical specification sections.

.2          Firestopping and smoke seals within mechanical (i.e. inside ducts, dampers) and 
                    electrical assemblies (i.e. inside bus ducts) shall be sealed under applicable
                    mechanical and electrical specifications sections. Firestopping and smoke seals
                    around outside of such mechanical and electrical assemblies, where they
                    penetrate fire rated separations, are the responsibility of this section.

1.3            RELATED SECTIONS

.1	    Division 15 - Mechanical: Mechanical work requiring firestopping.

.2	    Division 16 - Electrical: Electrical work requiring firestopping.

1.4             REFERENCE STANDARDS

.1     ANSI/UL 1479 - Fire Tests Of Through-Penetration Firestops

1.5           SYSTEM DESCRIPTION

.1     Firestopping Materials: Provide firestopping system(s) of sufficient thickness, width
                and density to provide and maintain a fire resistance rating, as indicated on 
                drawings and in accordance with UL or FM design numbers.

.2     Provide a seal completely filling all annular spaces to prevent the passage of flame,
                smoke and gases through the opening in the fire separation in which it is installed.

.3     Material Compatibility: Provide materials which are compatible with all materials
                used in the system including materials used in or on penetrants as well as all
                construction materials used in conjunction or contiguous with the system.

.4     Accessories: Provide components for each firestopping system that are needed
                to install fill materials. Use only components specified by the firestopping 
                manufacturer and approved by the qualified testing and inspecting agency for
                the designated fire resistance rated systems.  Accessories include but are not 
                limited to the following items:

Permanent forming/damming/backing materials.
      Temporary forming materials.
      Substrate primers.
      Collars.
      Steel sleeves.

1.6          SUBMITTALS

.1      Manufacturer’s Data: Submit manufacturer’s specifications, installation instructions
                 and product data for each material required, in accordance with Section 01300. 
                 Include manufacturer’s certification, if requested and UL, WH, ULC, cUL or FM test
                 reports to show compliance with the Contract Documents.

.2     Shop Drawings: Submit shop drawings showing typical installation details including 
                 reinforcement, anchorage, fastenings and method of installation for each type of
                 firestopping condition.

.3      Samples: If requested, submit samples of each type of firestopping systems, smoke
                seals and accessories. Indicate location where material/system shall be utilized.

1.7           QUALITY ASSURANCE

.1     Manufacturer: Company specializing in manufacturing products of this Section with
                minimum three (3) years documented experience.

.2     Applicator: Company having a minimum of three (3) years experience in the 
                 installation of materials specified herein on projects comparable to this Project. 
                The firm shall have the written approval of the firestopping material 
                 manufacturer(s).

1.8           REGULATORY REQUIREMENTS

.1     Conform to applicable local Building Codes for fire resistance ratings.

.2     Provide materials, accessories and application procedures which have been listed
                by UL, FM or tested by a nationally recognized independent testing
                agency according the ANSI/UL 1479 or ASTM E814 to achieve the 
                required fire protection rating.

1.9           ENVIRONMENTAL REQUIREMENTS

.1     Do not proceed with the installation of firestopping materials when temperatures or 
                weather conditions exceed the manufacturer’s recommended limitations for
                installation.

.2     Ventilate solvent based firestopping per firestopping manufacturer’s instructions
                 by natural means or, where this is inadequate, forced air circulation.

1.10        DELIVERY, STORAGE AND HANDLING

.1     Deliver materials to Site in manufacturer’s sealed and labelled containers intact. 
                Handle and store materials in accordance with manufacturer’s instructions.

1.11         PROJECT/SITE CONDITIONS

.1     Comply with manufacturer’s recommended requirements for temperature, relative
                 humidity and substrate moisture content during application and curing of materials.

1.12        SEQUENCING AND SCHEDULING

.1     Do not install firestopping system(s) until Work within opening has been completed. 
                Coordinate with other applicable Sections. Schedule work of other trades so that 
                firestopping applications can be inspected prior to being covered by subsequent
                construction.

2               Products

2.1           ACCEPTABLE MANUFACTURERS

.1     Provide firestopping silicone sealants, water-based sealants, mortars, or firestop 
                devices from the following manufacturer:

A/D Fire Protection Systems Inc.

2.2           MATERIALS

.1     Provide a complete system of asbestos-free firestopping and through-penetrations           firestopping. Firestop systems capable of maintaining an effective barrier against flame, smoke and gases in compliance with requirements of ANSI/UL 1479 or ASTM E814 and listed by UL or FM and in addition are approved by jurisdictional authorities and the Consultant.

.2     A/D FIREBARRIER Silicone Sealants: For use in openings 304.8 mm dia. or greater
                but not to exceed opening sizes for which they are intended, penetrations subject to
                movement, in control joints, in curtain wall joints, as a sealant for smoke barrier
                construction, fire and smoke dampers, head of wall details and fire doors in 
                masonry or gypsum wall partitions.

.3     A/D FIRBARRIER Mortar: For use in large openings, in static, non-moving,
                penetrations such as cable trays, electrical and communication bundles, conduit 
                and non-combustible sleeves and rated insulated pipes.

.4     Firestopping for Combustible Penetrating Items: For use in openings where either
                plastic pipe, non-rated insulated pipes or insulated cables are installed.

.5     Firestop system ratings: Comply with  Building Code (BOCA) requirements for 
                locations and hourly ratings of F, FT, FH and FTH designations.

2.3           ACCESSORIES

.1     Damming and backup materials, supports and anchoring devices: Non-combustible,
                to manufacturer’s recommendations and in accordance with the tested system being
                installed as acceptable to jurisdictional authorities.

.2     Retainers: Galvanized clips approved by manufacturer to hold A/D FIREBARRIER
                Mineral Wool insulation in place.

.3     Primers: As required by firestopping manufacturer and compatible with selected
                system and contiguous materials.

.4     Water: Potable.

.5     Sealants for vertical joints: Non-sagging.

.6     Sealants and fluid seals at floor openings: Self-levelling.

.7     Sealants and putty for vertical and overhead joints: Non-sagging.

.8     Tape: Pressure sensitive masking tape as recommended by the firestopping 
                 manufacturer.

3               Execution

3.1           EXAMINATION

.1     Examine substrates, openings, voids, adjoining construction and conditions under 
                which the Work is to be installed. Confirm compatibility of surfaces scheduled to 
                receive firestopping.

.2     Verify that penetrating elements are securely fixed and properly located with the
                 proper space allowance between penetrations and surfaces of openings.

.3     Do not proceed with Work until unsatisfactory conditions have been corrected.

3.2           PREPARATION

.1     Surfaces to receive firestopping shall be free of dirt, dust, grease, oil, rust, loose 
                 materials, form release agents, frost, moisture or any other matter which would
                 impair the bond of firestopping material to the substrate of penetrating item(s).

.2     Prime substrates in accordance with manufacturer’s written instructions or
                recommendations.  Confine primers to areas of bond; do not allow spillage or
                migration onto exposed surfaces.

.3     Do not apply firestopping and smoke seals to surfaces previously painted or treated 
                with sealers, curing compounds, water repellent or other coatings unless tests have
                been performed to ensure compatibility of materials. Remove coatings as required.

.4     Ensure that anchoring devices, back-up materials, clips, sleeves, supports and 
                other related materials used in the actual fire tests are provided.

.5     Mask where necessary to prevent firestopping materials from contacting adjoining 
                surfaces that will remain exposed upon completion of Work. Remove tape as soon
                as it is possible to do so without disturbing firestopping’s seal with substrates.

.6     Installation is not to proceed until submittals have been completed.

3.3           INSTALLATION

.1     Manufacturer’s Instructions: Comply with UL or FM Listings and 
                manufacturer’s instructions for the type of material and condition of opening in 
                each case. Consult with the manufacturer’s technical representative to determine
                proper procedure for conditions not fully covered by printed instructions. Record 
                in writing any oral instructions received, with copy to manufacturer.

.2     Install firestopping with sufficient pressure to properly fill and seal openings to 
                ensure an effective smoke seal. Tool or trowel exposed surfaces. Remove 
                excess firestopping material promptly as the Work progresses and upon 
                completion.

.3     Damming: Provide leak-proof dams as required to seal openings and contain
                 liquid sealants, putty or mortar until cured. Install damming in accordance with 
                 manufacturer’s instructions.

.4     Damming Boards: Install forming/damming materials and other accessories of
                 type required to support fill materials during their application and in the position
                 needed to produce the shapes and depths required to achieve fire ratings of
                 through-penetration firestop systems.

Combustible Type: For temporary dams only. Remove after firestopping material 
                 has cured.

Non-Combustible Type: For temporary or permanent dams. Provide 
                non-combustible type wherever damming material cannot be removed after
                applying firestopping materials.

.5     Void Filler: Use materials recommended by the firestopping manufacturer to seal 
                 gaps created by non-combustible type damming boards and to seal around 
                 cables, conduits, pipes and where void filler material becomes part of the fire
                 rated assembly.

.6     Sealant: Install damming material or mineral wool as required. Apply sealant so
                air voids are not present and sealant is in full contact with penetrating items. 
                Tool sealant to ensure substrate contact. Remove excess sealant in accordance
                with manufacturer’s recommendations.

.7     Mortar: Install damming material as required. Mix mortar in strict accordance with 
                manufacturers instructions. Pump, trowel or hand pack mortar through openings
                to minimum thickness as recommended by manufacturer and as listed by UL
                or FM, to achieve required fire rating.

.8     Firestopping Mineral Wool: Install firestopping by compressing material to the 
                minimum required by UL or FM listing. Apply firestopping in 
                sufficient thickness, depth and density so as to achieve the required fire 
                resistance rating. Use impaling clips to support and secure firestopping where
                required by tested system.

3.4         FIELD QUALITY CONTROL

.1     Notify Consultant when completed installations are ready for inspection prior to 
                concealing or enclosing an area containing firestopping materials.

.2     Arrange for inspections by the Owners independent inspection and testing
                company, appointed and paid for by Owner.

.3     Following field inspections, provide all repair as required to ensure compliance
                with the Contract Documents.

3.5          CLEANING AND PROTECTION

.1     Upon completion of this work, remove all materials, equipment and debris from the
               site.

.2     Leave work area and adjacent surfaces in a condition acceptable to the Consultant.

.3     Leave installed work with sufficient protection to enable it to remain untouched until 
               project turnover.

End of Section