# MEMORANDUM

**TO:** Jean Fraser, Planner

**FROM:** David Senus, P.E. & Ashley Auger, E.I.T.

**DATE:** November 6, 2012

**RE:** 321 Commercial St. Mixed Use Development, Level III Final Site Plan/Subdivision Application

Woodard & Curran has reviewed the Level III Final Site Plan/Subdivision Application for the Mixed Use Development located at 321 Commercial Street in Portland, Maine. The project consists of development of a six story mixed use building with a 131 room hotel, 7,000 Square-Feet (SF) of restaurant space, and 14 residential units on the site of an existing gravel surface parking lot. The project proposes a net increase of 2,513 square feet of impervious area on the site.

**Documents Provided By Applicant**

* Level III Site Plan/Subdivision Application and attachments dated October 22, 2012, prepared by Opechee Construction Corporation, on behalf of J.B. Brown & Sons.
* Engineering Plans, Sheets C01-C13, CMTC, S01 & CP01-CP04, dated October 22, 2012, prepared by Opechee Construction Corporation, on behalf of J.B. Brown & Sons.

**Comments**

1. In accordance with Section 5 of the City of Portland Technical Manual, a Level III development project is required to submit a stormwater management plan pursuant to the regulations of Maine DEP Chapter 500 Stormwater Management Rules, including conformance with the Basic, General, and Flooding Standards:
   1. Basic Standards: Plans, notes, and details have been provided to address erosion and sediment control requirements, inspection and maintenance requirements, and good housekeeping practices in accordance with Appendix A, B, & C of MaineDEP Chapter 500.
   2. General Standards: The project primarily includes re-development of existing impervious areas. However, the project does include 2,513 square feet of new impervious area. Redevelopment of the existing impervious areas of the site qualifies for an exemption from meeting the General Standards; however, the Applicant must provide stormwater treatment in accordance with the General Standards for an area equivalent to the proposed 2,513 square feet of new impervious area. Inspection and maintenance of any proposed stormwater quality treatment features will need to be included in the Inspection and Maintenance Plan in accordance with and in reference to MaineDEP Chapter 500 guidelines and Chapter 32 of the City of Portland Code of Ordinances
   3. Flooding Standard: The project will result in approximately 2,513 SF of new impervious surface. The Applicant has submitted a detailed stormwater model indicating a minor increase in post-development runoff rates for the project relative to pre-development conditions during certain storm events. Stormwater from the project site will enter the City storm drain system which ultimately discharges to the tidal Fore River, a tributary to Casco Bay (the Atlantic Ocean). Projects that discharge to the Ocean are eligible for a waiver from the Flooding Standard. The project qualifies for a waiver from meeting the flooding standard so long as the City of Portland Department of Public Services confirms capacity to accept the minor increase in flow into the City storm drain system.
2. The following details should be provided for work within the City Right-of-Way, in accordance with the City of Portland Technical Manual:
   1. A brick driveway apron with bituminous base, per Figure I-11
3. Please clarify the use of the “Catch Basin Inlet” detail versus the “Precast Catch Basin” detail (Sheet C11). Unless unique situations warrant, the City would require the “Precast Catch Basin” detail with 3’ sump & outlet trap.