From: 	Chris Pirone
To:	JF@portlandmaine.gov
Date: 	10/9/2013 9:53 AM
Subject: 	Fwd: Re: 133 York-  need comments today please
Attachments:	Re: 133 York-  need comments today please

Jean,

It appears from the plans FIRE comments are not being met per NFPA.

The applicant will need to show that our largest fire apparatus can get access to the front of the building and operate with 20' access in front of the building for emergency operations.

Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410

From: 	Chris Pirone
To:	JF@portlandmaine.gov
Date: 	10/9/2013 10:08 AM
Subject: 	Fwd: Re: 133 York-  need comments today please
Attachments:	Re: 133 York-  need comments today please

Jean,

To clarify the needed 20' in front of the building it must be measured from the furthest point of the building not just at ground level.

Also, the applicant has not indicated through their NFPA site code analysis if a private fire hydrant will be needed to meet fire flow requirements for the building.

Tim did state they will meet all applicable codes and the fire hydrant may be resolved later.

Captain Chris Pirone
Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410