## MS-9200UDLS
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 7.22.14
Note 2: Use the dropdowns and the yellow cells to enter values.
MS-9200UDLS Rev.3 Battery Calculation
Secondary Power Source Requirements | [11 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.145 | = | 0.145 | 1 | x | 0.275 | = | 0.275 |  | 25 Minutes | 0.417 | 90 Hours | 90
XRM-24B | 0 | x | 0 | = |  | 0 | x | 0 | = |  |  | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 45 Minutes | 0.75
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  |  | 60 Minutes | 1
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
ECC-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
ANN-BUS Devices
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-LC | 0 | x | 0.15 | = |  | 0 | x | 0.15 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 1 | x | 0.025 | = | 0.025 | 1 | x | 0.064 | = | 0.064
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
BEAM1224 | 0 | x | 0.017 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 14 | x | 0.0003 | = | 0.0042
SD355T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H355R | 32 | x | 0.0003 | = | 0.0096
H355HT | 8 | x | 0.0003 | = | 0.0024
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 3 | x | 0.0004 | = | 0.0012
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 12 | x | 0.0003 | = | 0.0036
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
B200SR | 0 | x | 0.001 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
EOLR-1 | 2 | x | 0.02 | = | 0.04 | 2 | x | 0.02 | = | 0.04
FCPS (Remote Sync) | [5 empty] | 1 | x | 0.0217 | = | 0.0217
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
Miscellaneous Devices
CO Detector | 2 | x | 0.02 | = | 0.04 | 2 | x | 0.04 | = | 0.08
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0.54 | = | 0.54
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #3 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #4 |  |  | 0 | = |  |  |  | 0 | =
Current Draw from TB3 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.271 | Total Alarm Load |  |  |  | 1.4207
MS-9200UDLS Rev.3 Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.271 |  |  | x | 24 |  | = | 6.504
Required Alarm Time in Minutes
15 Minutes
Alarm Load Current (Amps) |  |  | 1.4207 |  |  | x | 0.25 |  | = | 0.35518
Total Current Load | [9 empty] | 6.8592
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 8.231
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the MS-9200UDLS Charger.
The batteries can be housed in the MS-9200UDLS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS 9200UDLS Control Panel:
The output current is within the panel's limitations.
MS-9200UDLS Rev.3 Circuit Detail
NAC/Output #1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
H/S | 6 | x | 0 | = | 0 | 6 | x | 0.09 | = | 0.54
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.54
NAC/Output #2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on J11: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on B15: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B23: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on J24: All eight ACM-8RF relays activated on a single module.
Note on J25: All annunciator LEDs on.
Note on J26: All annunciator LEDs on.
Note on J27: All annunciator LEDs on.
Note on J28: All annunciator LEDs on.
Note on J29: All annunciator LEDs on.
Note on J30: All annunciator LEDs on.
Note on J31: All annunciator LEDs on.
Note on J32: LDM-32F with LEDs on.
Note on E73: Refer to the Device Compatibility Document for standby current.
Note on B74: Only add those devices that are drawing power from the MS-9200UDLS Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B80: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B86: Use Circuit Detail Worksheet below for configuring Output Circuits.
Note on B91: The total standby current must include both the nonresettable/resettable (TB1 Terminals 1 & 2) and resettable (TB1 Terminals 3 & 4) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 & TB4 circuits is 2.5 amps per NAC Output and 1.0 amps per special application auxiliary power output.
Note on H100: Select Standby Time in Hours from the dropdown list.
Note on H103: Select the Alarm Time in minutes from the dropdown list.
Note on H106: Select the Derating Factor from the dropdown list.