To: Ben Wallace, Jr., Fire Prevention Officer

Portland Fire Dept.

Re: Fire Alarm sequence of operation                                           January 31st. 2012

Whenever an initiating device, waterflow, smoke detector, or manual pull station is

activated, this in turn will sound the notification device located in rear of the building & transmit the alarm to Central Station. The notification device is one horn/strobe in rear stairwell.

Sprinkler riser is in cellar. Smoke detector & pull station are above Fire panel inside first floor rear entry door where Knox box is located.

The procedure for the Fire Dept. when they arrive on site will be to go to the rear of the building and determine which device was activated. Pull station will show alarm, smoke detector will have a steady red light & sprinkler will have water bell sounding.

To silence the notification device, press acknowledge silence once then press a second time to silence horn/strobe. When alarm has been resolved the rest switch will clear all circuits and system will be normal.