| Business Name/Owner/Mgr/Location | Inspector | BENJAMIN WALLACE JR |  | Inspection Date |
| --- | --- | --- | --- | --- |
| 655-661 CONGRESS STREET |  |  |  | 11/19/2009 |  |
|  | Building Number | CBL | Inspection Type |  |
|  | 1147 |  | 046 D021001 | INSPECTION |

- High-rise building- A supervised, automatic sprinkler system and class 1 standpipe is required (101-11.8 and 101-31.3.5).

- Fire alarm system shall be installed and maintained in accordance with NFPA 72 (101-9.6.1.4).  Produce inspection, test and compliance documentation from an approved service company.

- Manual Pull stations are required at exits (101-31.3.4.2).

- System smoke detectors are required in egress areas (Chapter 2.5-23).

- Commercial tenants are not covered by fire alarm system (101-6.1.14.2).

- Exit corridor doors do not meet code (101-31.3.6).

- Transom windows are not permitted in egress corridors (101-31.3.6.5).

- Storage is not permitted in the egress: rear stairs (101-7.1.10)

- Hazardous areas shall be protected: including laundry, electrical and trash rooms (101.3.2.1).

- Stair signage is required (101-7.2.2.5.4).

- The rear stair at the second floor in not illuminated (101-31.2.8), and exit signage must be provided to indicate the exit path (101-31.2.10).

- Fire extinguishers are required at each exit on each floor, and with in 75 feet of travel in the corridors; and shall be with in 30 feet of travel of all hazardous areas (101-31.3.5.7).

- The first floor of the front stair and the out of service elevator at the rear stair are unprotected vertical openings (101-31.1).

- Numerous violations of the Electrical Code were observed by City Electrical Inspector Mike Menario; especially in the basement.  Certify electrical system (101-31.5.1 and City Code Chapter 6).