SECTION 11175

WASTE CHUTES

1. 	GENERAL:

1.1	REFERENCES

A.	Drawings and general provisions on Contract, including General Conditions and 				Division 1 specifications, apply to work in this section.

B. 	Gypsum Board:  Section 09250

1.2 	DESCRIPTION OF WORK

A. 	Furnish and install, where shown on Drawings, a 24" diameter Rubbish Chute as 			manufactured by Wilkinson Chutes, or equal as specified below.

1.3	QUALITY ASSURANCE

A.	The work in this section shall be subject to all applicable provisions of governing 			building codes and ordinances.

1.4 	SUBMITTALS

A. 	Product Data:  Submit manufacturer’s product specifications, performance data sheets, 		and installation instructions.

B. 	Shop Drawings:  Submit plans, elevations, and details for work not fully shown by 			published product data; include rough-in dimensions and service connections.

1.5	PRODUCT DELIVERY, STORAGE AND HANDLING

A.	Protection:  Equipment shall be protected at all times from physical damage, dirt, water, 		etc.

2.  	PRODUCTS

2.1	CHUTE MATERIAL:  The Chute shall be fabricated of #16 U.S. Gauge Aluminized Steel.

2.2	INTAKES:

A.	15" wide x 18" high, stainless steel, thru-pivot shaft, self-closing, positive latching, bottom hinged, hand operated doors bearing 1-1/2 Hr., 650º F. U.L. “B” label drywall installation.

B.	Provide removable stainless steel door trim with embossed (RUBBISH) letters.

2.3	DISCHARGE:  Type “A” open end inclined rolling door with fusible link hold-open.  Fabricated, insulated “B” label construction even though U.L. Label is not required.

2.4	FLOOR FRAMES:  Fabricate floor frames of 1-1/2 x 1-1/2 x 3/16 angles and 1-1/2  x 3/16 bar stock welded assemble.

2.5	SPRINKLERS:  1/2" IPS 155º sprinkler head above top intake.  Addition 1/2" sprinklers at every second intake (or as required by Code).  3/4" IPS flushing spray head located in channel above top intake ready for connection by plumber.

2.6	VENT:  Provide full diameter vent through roof 4'-0" above roof with metal explosion cap.

3. 	EXECUTION:

3.1	INSPECTION

A. 	Inspect the areas and conditions under which chute is to be installed.  Do not proceed 		with the work until conditions are satisfactory.

3.2	INSTALLATION

A.	Chute shall be installed in accordance with approved drawings.

3.3	TESTING AND INSTRUCTIONS

A.	Test operation of equipment.  Provide maintenance manual.  Instruct Owner’s operation 		personnel in proper use and maintenance of equipment.

END OF SECTION