Legalization of 92 Clark Street

All spaces:

- All fire door assemblies shall be labeled 60-minute fire assemblies (remove paint from labels).  All fire doors shall be self-closing.

- Each unit door shall be labeled (ie: 1F, 1R, 2, 3).

- Address number shall be visible on front of building and contrasting with background.

Basement:

- Boiler protection required (sprinkler head(s)).

- Certify electrical system (letter of compliance required from licensed electrician and electrical permit may be required).

- Kraft paper on insulation shall not be exposed.

Unit 1F:

Pass

Unit 1R:

- CO alarm required.

- Remove door between kitchen and living room (shall not be bedroom unless smoke alarm is installed).

Unit 2:

- Co alarm required

Unit 3:

- Smoke and CO alarms required.

- Storage shall not be allowed in the egress stairs or room adjoining the egress stairs unless those rooms have a 60-minute fire door assembly.  Owner plans to move unit 3 fire door assemblies to the landings on the second floor to remedy this.