**NOTICE OF VIOLATION**

**AND ORDER TO CORRECT**

August 2, 2016

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Violator 1:**  Rising Tide Properties, LLC  395 Old Stage Road  Arrowsic, Maine 04530 | | **Violator 2:**  Ebb Tide Properties, LLC  c/o C. Alan Beagle  P.O. Box 7044  Portland, Maine 04112 | | |
| **Violator 3:**  Bellport Property Management  563 Washington Avenue  Portland, Maine 04103 | |  | | |
| **Location:**  266 Danforth Street | **CBL:**  057 F004001 | | **Inspection Date:**  7/15/2016 |
| **Inspector:**  Steven Hall | **Inspection Type:**  Fire Company – FP Routine | | **Status:**  Failed |

The City of Portland Fire Department inspected this property, and found the fire and life safety code violations listed below, which you are hereby ordered to correct. You must complete the proposed plan of action column by proposing a reasonable timeframe to remedy each violation. This form must be received by the Fire Prevention Bureau no later than **August 15, 2016.** The Bureau reserves the right to reject or modify any proposed plan of action, and may require evidence of sufficient financial and technical capacity to complete the proposed plan. Please contact the Bureau with any questions.

**YOUR FAILURE TO SUBMIT A PLAN OF ACTION BY THE DATE PROVIDED,**

**OR TO CORRECT ANY VIOLATION WITHIN THE APPLICABLE TIME FRAME, MAY RESULT IN LEGAL ACTION AGAINST YOU, THE IMPOSITION OF CIVIL PENALTIES, AND THE PURSUIT OF OTHER LEGAL REMEDIES.**

|  |  |
| --- | --- |
| **Violation** | **Proposed Plan of Action** |
| 1. NFPA 101- 31.3.4.5.1 SMOKE ALARMS REQUIRED.   In buildings other than those equipped throughout with an existing, complete automatic smoke detection system, smoke alarms shall be installed in accordance with 9.6.2.10, as modified by 31.3.4.5.2, outside every sleeping area in the immediate vicinity of the bedrooms and on all levels of the dwelling unit, including basements.  *Smoke alarm missing in basement. Immediately install temporary alarm in basement and provide for full system installation.* | **IMMEDIATELY** install temporary alarm in basement. Your signature below indicates that a temporary alarm has already been installed.  Date of completion for full permanent installation: |
| 1. NFPA 1 EXCESSIVE/DISORDERLY STORAGE. Reference NFPA 1 for excessive fuel load.   *Remove storage on rear stairs.* |  |
| 1. NFPA 70 MISSING BOX COVERS.   Refer to NFPA 70, National Electrical Code, on standards for missing box covers.  *Install junction box cover in basement.* |  |
| 1. NFPA 101- 31.3.2.1.1 BOILER PROTECTION REQUIRED.   The areas described in table 31.3.2.1.1 shall be protected as indicated: boiler and fuel-fired heater rooms serving more than a single dwelling unit (minimum separation/protection is 1 hour or sprinklers).  *Install sprinkler head over water heaters.* |  |
| 1. NFPA 1, CHAPTER 10 - 10.1 1.6 HIBACHI OR GRILL ON BALCONY.   No hibachi, gas-fired grill, charcoal grill, or other similar devices used for cooking, heating, or other purpose, shall be used or kindled on any balcony or under any overhang portion or within 10 ft of any structure.  *Remove grill from second floor balcony.* |  |
| 1. NFPA 101- 8.3.4.2 60 MINUTE FIRE DOOR REQUIRED.   Refer to NFPA 101- table 8.3.4.2 that states fire door assemblies for vertical shafts (including stairways, exits, and refuse chutes) are rated and required for 1 hour.  *Install fire rated doors on all apartments.* |  |

*You may appeal this Notice of Violation and Order to Correct to the City of Portland Zoning Board of Appeals within ten business days of this decision, pursuant to the City of Portland Code of Ordinances § 10-23. Your failure to appeal may result in you being barred in the future from challenging the determinations of City of Portland Fire Prevention Bureau contained in this notice.*

**VIOLATOR CERTIFICATION**

I agree to remedy the violations listed within the timeframes provided. If I require additional time to comply, I understand that I must contact the Fire Prevention Bureau prior to the deadline to request an extension, which is entirely within the Bureau’s discretion to grant or deny. If I fail to comply with this agreement, I understand that I am liable for penalties pursuant to the City of Portland Code of Ordinances §§ 1-15 and 10-25, and 30-A M.R.S. § 4452 and may be subject to further legal action.

\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date Violator 1

\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date Violator 2

\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date Violator 3

**SEEN AND AGREED**

\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date Fire Prevention Bureau