124 Emery Street

* All units will need a hard wired photo electric/battery back-up smoke detector installed in each bedroom.
* All units will need a hard wired photo electric/battery back-up combination smoke/carbon monoxide detector installed in the common area (living room or foyer) of each unit.
* Missing and/or dated smoke detectors in the hallways and stairwells will need to be replaced.
* The basement will need to be cleaned of debris and trash.
* Electrical junction boxes in the basement will require a cover.
* Old non powered electrical wires and fuse boxes in the basement will need to be removed.
* Exposed electrical wires in the rear hallway (bottom of stairwell) will need to be placed in an approved electrical box or have a light connected.
* Access to the electrical panels in the basement will need to be improved by eliminating wall separation
* All units should be clearly numbered on the doors.