| FIELD REPORT #11 SRG Engineering, Inc. P. O. Box 925 Gray, ME 04039-0925 Tel :(207)-657-7323 Fax :(207)-657-7342 | Project No.:07-003 Date: May 7, 2007 Project Name: Mercy Hospital Project Location: Portland, Maine Weather Conditions: Sunny, 60’s-Windy Contact Person(s): Steven Grant-SRG Eng. Jim Lanza-Gilbane Co. James-CCB Mike Drew-QAL |
| --- | --- |
| Discussion/Observations: LEVEL 4: GRID 1 TO 3; A to H Line | Copies To: Sean Welty-KLMK Roger Domingo-SWC James Lanza-Gilbane Paul Stevens-SMRT Janusz Wszola (EOR)-SMRT Cathy Streifel-SMRT |
| Comments: Mike Drew (QAL) was present with me at the time of our site walk/observation. Decking Attachments: There are a couple locations marked in blue ribbon (by QAL) for incomplete side lap and decking welds. Action Required: Contractor to correct prior to placement of concrete. I told this to Mike (CCB) about these flagged areas before departure. He indicated these would be corrected before concrete placement. Diagonal Bracing Connections: Brace connections still in progress. Shear Studs: Observations noted indicate stud size, location(s), quantity, and spacing comply with project documents. Perimeter deformed reinforcement: Observations noted indicate location(s), size, and spacing comply with project documents. Interior deformed reinforcement: Observations noted indicate location(s), size, and spacing comply with project documents. Slab WWF reinforcement: Observations noted indicate it complies with project documents. Structural Steel: Please refer to QAL report No. QAL-07-0797 for items that must be addressed. Jim Lanza indicated concrete for 4th floor, this section, to be placed Tuesday May 8th morning. |
| Diagrams: (Attached Photos 1 through 17) |  |
| C: File | Signed: ___________________________________ |

- 1 of  1-