| FIELD REPORT #12 SRG Engineering, Inc. P. O. Box 925 Gray, ME 04039-0925 Tel :(207)-657-7323 Fax :(207)-657-7342 | Project No.:07-003 Date: May 14, 2007 Project Name: Mercy Hospital Project Location: Portland, Maine Weather Conditions: Sunny Contact Person(s): Steven Grant-SRG Eng. Jim Lanza-Gilbane Co. |
| --- | --- |
| Discussion/Observations: LEVEL 4: GRID 3 TO 5; A to H Line | Copies To: Sean Welty-KLMK Roger Domingo-SWC James Lanza-Gilbane Paul Stevens-SMRT Janusz Wszola (EOR)-SMRT Cathy Streifel-SMRT |
| Comments: Decking Attachments: There were no locations observed with incomplete side lap and decking welds. Action Required: None. Diagonal Bracing Connections: Brace connections still in progress. Shear Studs: Observations noted indicate stud size, location(s), quantity, and spacing comply with project documents with the following exceptions: W16x31 on Grid Line 3, A to B: Six (6) shear studs on the South end are located on the “weak rib” side of the deck flute. These studs were painted orange by SRG. Action Required: Either remove each and replace in the correct location, or add 3 new studs on the correct (strong) side of the deck flute. W16x31 about 16 feet West of Grid Line 3, A to B: One (1) shear stud on the South end is located on the “weak rib” side of the deck flute. This stud was painted orange by SRG. Action Required: Either remove and correctly replace it in the correct location, or add 3 new studs on the correct (strong) side of the deck flute. Perimeter deformed reinforcement: Observations noted indicate location(s), size, and spacing comply with project documents. Interior deformed reinforcement: Observations noted indicate location(s), size, and spacing comply with project documents. Slab WWF reinforcement: Observations noted indicate it complies with project documents. Structural Steel: There were no locations observed with incomplete and/or missing connections. Action Required: None. Jim Lanza informed SRG on May 23rd that concrete for the 4th floor, this section, to be placed next Friday, June 1st. Jim Lanza informed SRG on May 23rd that the slab-on-grade is anticipated to be placed Wednesday, May 30th. |
| Diagrams: (Attached Photos 1 through 23) |  |
| C: File | Signed: ___________________________________ |

- 1 of  1-