| ##### FIELD REPORT #13 SRG Engineering, Inc. P. O. Box 925 Gray, ME 04039-0925 ### Tel :(207)-657-7323 Fax :(207)-657-7342 | Project No.:07-003 Date: May 31, 2007 Project Name: Mercy Hospital Project Location: Portland, Maine Weather Conditions: Overcast, occ’l light mist Contact Person(s): Steven Grant-SRG Eng. Mike Drew-QAL James-CCB |
| --- | --- |
| Discussion/Observations: LEVEL 5: GRID 1 TO 4.7; A to H Line | Copies To: Sean Welty-KLMK Roger Domingo-SWC James Lanza-Gilbane Paul Stevens-SMRT Janusz Wszola (EOR)-SMRT Cathy Streifel-SMRT |
| Comments: - Decking Attachments: There were no locations observed with incomplete side lap and decking welds. Action Required: None. - Diagonal Bracing Connections: Brace connections still in progress. NOTE: Brace low-end at grid H-2 must be welded prior to placement of concrete for Level 5. Action Required: Be sure all low-end brace welds are provided, inspected by Quality Assurance Labs, and approved prior to placing concrete. - Shear Studs: Observations noted indicate stud size, location(s), quantity, and spacing comply with project documents with the following exceptions: - W21x62 on Grid A, 4 to 4.7 line: This beam has no (0) shear studs while plans indicate 13 required. Action Required: Provide 13 studs on beam per contract plans. - W30x108 on Grid Line H, 2 to 3 Line: 68 studs required, 65 provided. Action Required: Add 3 studs. - W21x62 on Grid 3, B to C Line: 32 studs required, 28 provided. Action Required: Add 4 studs. - Perimeter deformed reinforcement with threaded end in Lenton couplers: Observations noted indicate location(s), size, and spacing comply with project documents with the following exceptions: (These areas were painted in orange.) - Missing one rebar at W36 beam on the diagonal from H-4 to F7-4.7. Action Required: Add missing rebar. - Column at A-4: Need 2 additional rebars and couplers at West side of column. Action Required: Add missing rebar and couplers. - Brace Gusset at mid-span of W36x330 at Grid A, 3 to 4 line: Need 2 additional rebars and couplers at each side of brace gusset. Action Required: Add missing rebars and couplers. - Brace Gusset at mid-span of W36x330 at Grid A, 3 to 4 line: Rebar not threaded into coupler at East side of gusset. Action Required: Add missing rebar. Replace coupler if needed since it is inclined downward. - Column at C-2: Need 2 additional rebars and couplers at North side of column. Action Required: Add missing rebar and couplers. - Columns at D-2, E-2, F-2: Need 2 additional rebars and couplers at each side of column. Action Required: Add missing rebar and couplers. - Column at G-2: Need 1 additional rebar and coupler at South side of column. Action Required: Add missing rebar and coupler. - Interior deformed reinforcement: Observations noted indicate location(s), size, and spacing comply with project documents. |  |
| Diagrams: (Attached Photos 1 through 23) |  |
| C: File | Signed: ___________________________________ |

- 1 of  2-