Subject: City inspection of fire and smoke seal at perimeter wall and floor, shaft chases, general walk through on 09-28-07.

Attendees: Chris Hanson; Mike Collins; Mike Menario;

From: Joe Bumps  Ledgewood Construction, Mercy MOB. Cell 415-7994, “e” mail jbumps@ledgewoodconstruction.com

Dave Bernier L/C,cell 615-4448, “e” mail dbernier@ledgewoodconstruction.com

() 1. Main lobby overhead beam w 16x26 between columns “D”&”E”&”2”&”3” not fireproofed per Architects drawing. Will ask Architect why beam does not have to be fireproofed.

() 2. It was noted that tenants with procedural or day surgery offices will change the building class and specification, such as fireproofing requirements.

() 3. Fire stop, Hilti applications need to be inspected by Hilti representative and signed off for properly installed.

() 4. Pipe penetrations through deck need to be smoke sealed, mineral wool or equivalent.

() 5. Present to city  slab/ wall fire and smoke detail. Detail enclosed in attachment.

() 6. Fire Chief at earliest convenience please meet on site to locate fire department connection and re-visit item 6 at last inspection. At stair towers the unused space under the stair stringers and treads at the basement and 1st floor can not be used for storage and is required to be sealed off with walls to prevent access. Drawing A-601 shows a metal railing that will prevent access to the space. The owner’s representative from LHF believes that the railing meets the code. (need to resolve.)