## GDI FINAL LAYOUT_FIRST_29032013
?Material List
Model | Qty | Description
RXYQ120PBTJ | 4 | Heat pump VRV P(B) R410A (208-230V)
RXYQ72PBTJ | 2 | Heat pump VRV P(B) R410A (208-230V)
FXAQ07PVJU | 75 | VRV A (P) - Wall Mounted Unit
FXAQ09PVJU | 4 | VRV A (P) - Wall Mounted Unit
FXAQ12PVJU | 12 | VRV A (P) - Wall Mounted Unit
KHRP26A22T | 18 | REFNET branch piping kit
KHRP26A33T | 5 | REFNET branch piping kit
KHRP26M22H | 8 | REFNET branch piping kit
KHRP26M33H | 5 | REFNET branch piping kit
KHRP26M72TU | 13 | REFNET branch piping kit
KHRP26M73TU | 2 | REFNET branch piping kit
DCM601A71 | 1 | intelligent Touch Manager (iTM)
BRC1E72 | 91 | Navigation Remote Controller 2013
BHFP22P100U | 3 | Outdoor Multi Connection Pipe Kit - VRV P Series HP
DCM601A72 | 1 | i-Touch Manager DIII Plus Adapter
Piping 1/4" | 2011.0ft
Piping 3/8" | 287.0ft
Piping 1/2" | 2065.0ft
Piping 5/8" | 524.0ft
Piping 3/4" | 125.0ft
Piping 7/8" | 28.0ft
Piping 1 1/8" | 359.0ft
Piping 1 3/8" | 85.0ft
Indoor Unit Details
SCU-1 - RXYQ192PBTJ
Name | FCU | Tmp C | TC | SC | Tmp H | HC
|  | Â°F | BTU/h | BTU/h | Â°F | BTU/h
101A BASEMENT:AC-1 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
201 B 3RD:AC-2 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
101A 2ND:AC-3 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
101B BASEMENT:AC-4 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
101B 1ST:AC-5 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
201A 2ND:AC-6 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
201A 2ND:AC-7 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
202A 2ND:AC-8 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
102A 1ST:AC-9 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
102B 1ST:AC-10 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
102B BASEMENT:AC-11 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
102A BASEMENT:AC-12 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
202A 2ND:AC-13 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
202B 2ND:AC-14 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
103B 1ST:AC-15 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
103A 1ST:AC-16 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
103 B BASEMENT:AC-17 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
103A BASEMENT:AC-18 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
203B 2ND:AC-19 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
203B 2ND:AC-20 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
104B 1ST:AC-21 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
104B 1ST:AC-22 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
203A 2ND:AC-23 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
104A 1ST:AC-24 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
203A 2ND:AC-25 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
104A 1ST:AC-26 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
1ST FL CORRIDOR WEST:C-1 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
2ND FLOOR CORRIDOR WEST:C-2 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
2ND FLR CORRIDOR CENTER WEST:C-5 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
Name | Condition 1 |  |  | Condition 2
| Suct | Disch | Airflow | Suct | Disch | Airflow
| Â°F | Â°F | cfm | Â°F | Â°F | cfm
AC-1 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-2 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-3 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-4 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-5 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-6 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-7 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-8 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-9 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-10 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-11 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-12 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-13 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-14 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-15 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-16 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-17 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-18 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-19 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-20 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-21 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-22 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-23 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-24 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-25 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
AC-26 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260
C-1 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290
C-2 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290
C-5 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290
Name | Sound | PS | MCA | MOP | WxHxD | Wght
| dBA |  | A |  | inch | lbs
101A BASEMENT:AC-1 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
201 B 3RD:AC-2 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
101A 2ND:AC-3 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
101B BASEMENT:AC-4 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
101B 1ST:AC-5 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
201A 2ND:AC-6 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
201A 2ND:AC-7 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
202A 2ND:AC-8 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
102A 1ST:AC-9 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
102B 1ST:AC-10 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
102B BASEMENT:AC-11 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
102A BASEMENT:AC-12 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
202A 2ND:AC-13 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
202B 2ND:AC-14 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
103B 1ST:AC-15 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
103A 1ST:AC-16 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
103 B BASEMENT:AC-17 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
103A BASEMENT:AC-18 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
203B 2ND:AC-19 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
203B 2ND:AC-20 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
104B 1ST:AC-21 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
104B 1ST:AC-22 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
203A 2ND:AC-23 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
104A 1ST:AC-24 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
203A 2ND:AC-25 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
104A 1ST:AC-26 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1ST FL CORRIDOR WEST:C-1 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2ND FLOOR CORRIDOR WEST:C-2 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2ND FLR CORRIDOR CENTER WEST:C-5 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
SCU-2 - RXYQ240PBTJ
Name | FCU | Tmp C | TC | SC | Tmp H | HC
|  | Â°F | BTU/h | BTU/h | Â°F | BTU/h
205 B 2ND:AC-27 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
105B 1ST:AC-28 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
205A 2ND:AC-29 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
105A 1ST:AC-30 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
106A BASEMENT:AC-31 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
106A AST:AC-32 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
204A 2ND:AC-33 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
106A BASEMENT:AC-34 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
204B 2ND:AC-35 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
106B 1ST:AC-36 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
206B 2ND:AC-37 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
108B 1ST:AC-38 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
106B BASEMENT:AC-39 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
108B BASEMENT:AC-40 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
204A 3RD:AC-78 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
204A 3RD:AC-79 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100
BASEMENT CORRIDOR CTR EAST:C-6 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
2ND FL CORRIDOR CENTER EAST:C-7 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
205A 2ND:AC-41 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
105A 1ST:AC-42 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
207A 2ND:AC-43 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
107A 1ST:AC-44 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
207A 2ND:AC-45 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
207A 2ND:AC-46 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
107 B 1ST:AC-47 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
207 B 2ND:AC-48 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
206A 2ND:AC-49 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
108A 1ST:AC-50 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
108A BASEMENT:AC-51 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
108A BASEMENT:AC-52 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
206A 3RD:AC-81 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
206A 3RD:AC-80 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
BASSEMENT CORRIDOR CTR WES:C-3 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
1ST FLOOR CORRIDOR CTR WEST:C-4 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000
Name | Condition 1 |  |  | Condition 2
| Suct | Disch | Airflow | Suct | Disch | Airflow
| Â°F | Â°F | cfm | Â°F | Â°F | cfm
AC-27 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-28 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-29 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-30 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-31 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-32 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-33 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-34 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-35 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-36 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-37 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-38 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-39 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-40 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-78 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-79 | 64.4 | 82.1 | 280 | 68 | 86.3 | 280
C-6 | 64.4 | 86 | 290 | 68 | 90.3 | 290
C-7 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-41 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-42 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-43 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-44 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-45 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-46 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-47 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-48 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-49 | 64.4 | 86 | 290 | 68 | 90.3 | 290
AC-50 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-51 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-52 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-81 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
AC-80 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260
C-3 | 64.4 | 86 | 290 | 68 | 90.3 | 290
C-4 | 64.4 | 86 | 290 | 68 | 90.3 | 290
Name | Sound | PS | MCA | MOP | WxHxD | Wght
| dBA |  | A |  | inch | lbs
205 B 2ND:AC-27 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
105B 1ST:AC-28 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
205A 2ND:AC-29 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
105A 1ST:AC-30 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
106A BASEMENT:AC-31 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
106A AST:AC-32 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
204A 2ND:AC-33 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
106A BASEMENT:AC-34 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
204B 2ND:AC-35 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
106B 1ST:AC-36 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
206B 2ND:AC-37 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
108B 1ST:AC-38 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
106B BASEMENT:AC-39 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
108B BASEMENT:AC-40 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
204A 3RD:AC-78 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
204A 3RD:AC-79 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
BASEMENT CORRIDOR CTR EAST:C-6 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2ND FL CORRIDOR CENTER EAST:C-7 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
205A 2ND:AC-41 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
105A 1ST:AC-42 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
207A 2ND:AC-43 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
107A 1ST:AC-44 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
207A 2ND:AC-45 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
207A 2ND:AC-46 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
107 B 1ST:AC-47 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
207 B 2ND:AC-48 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
206A 2ND:AC-49 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
108A 1ST:AC-50 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
108A BASEMENT:AC-51 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
108A BASEMENT:AC-52 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
206A 3RD:AC-81 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
206A 3RD:AC-80 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
BASSEMENT CORRIDOR CTR WES:C-3 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
1ST FLOOR CORRIDOR CTR WEST:C-4 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
SCU-3 - RXYQ192PBTJ
Name | FCU | Tmp C | TC | SC | Tmp H | HC
|  | Â°F | BTU/h | BTU/h | Â°F | BTU/h
110A BASEMENT:AC-61 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
110B 1ST:AC-62 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
110B 1ST:AC-63 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
110A 1ST:AC-64 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
209A 2ND:AC-65 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
110B BASEMENT:AC-66 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
111B BASEMENT:AC-67 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
111A BASEMENT:AC-68 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
111B 1ST:AC-69 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
209A 2ND:AC-70 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
111A BASEMENT:AC-71 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
209A 2ND:AC-72 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
209A 2ND:AC-73 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
112B 1ST:AC-74 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
210B 2ND:AC-75 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
112B BASEMENT:AC-76 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
112A 1ST:AC-77 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
208 A 2ND:AC-53 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
208A 2ND:AC-54 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100
208A 2ND:AC-55 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
109A AST:AC-56 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
2ND FL CORRIDOR EAST:C-9 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100
1ST FL CORRIDOR EAST:C-10 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100
208 B 2ND:AC-57 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
208B 2ND:AC-58 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
109B 1ST:AC-59 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
109B 1ST:AC-60 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
2ND FL CORRIDOE CTR EAST:C-8 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700
Name | Condition 1 |  |  | Condition 2
| Suct | Disch | Airflow | Suct | Disch | Airflow
| Â°F | Â°F | cfm | Â°F | Â°F | cfm
AC-61 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-62 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-63 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-64 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-65 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-66 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-67 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-68 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-69 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-70 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-71 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-72 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-73 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-74 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-75 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-76 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-77 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-53 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-54 | 64.4 | 85.7 | 280 | 68 | 90 | 280
AC-55 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-56 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
C-9 | 64.4 | 85.7 | 280 | 68 | 90 | 280
C-10 | 64.4 | 85.7 | 280 | 68 | 90 | 280
AC-57 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-58 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-59 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
AC-60 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
C-8 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260
Name | Sound | PS | MCA | MOP | WxHxD | Wght
| dBA |  | A |  | inch | lbs
110A BASEMENT:AC-61 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
110B 1ST:AC-62 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
110B 1ST:AC-63 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
110A 1ST:AC-64 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
209A 2ND:AC-65 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
110B BASEMENT:AC-66 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
111B BASEMENT:AC-67 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
111A BASEMENT:AC-68 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
111B 1ST:AC-69 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
209A 2ND:AC-70 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
111A BASEMENT:AC-71 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
209A 2ND:AC-72 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
209A 2ND:AC-73 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
112B 1ST:AC-74 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
210B 2ND:AC-75 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
112B BASEMENT:AC-76 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
112A 1ST:AC-77 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
208 A 2ND:AC-53 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
208A 2ND:AC-54 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
208A 2ND:AC-55 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
109A AST:AC-56 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2ND FL CORRIDOR EAST:C-9 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1ST FL CORRIDOR EAST:C-10 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
208 B 2ND:AC-57 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
208B 2ND:AC-58 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
109B 1ST:AC-59 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
109B 1ST:AC-60 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2ND FL CORRIDOE CTR EAST:C-8 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
Outdoor Unit Details
Name | Model | Comb | Tmp C | CC | Tmp H | HC | Piping | Bse Refr | Ex Refr
|  | % | Â°F | BTU/h | Â°F | BTU/h | ft | lbs | lbs
SCU-1 | RXYQ192PBTJ | 120 | 87.1 | 208604 | 8.0 / 50% | 152204 | 233.1 | 38.6 | 34.5
SCU-2 | RXYQ240PBTJ | 124 | 87.1 | 265227 | 8.0 / 50% | 173602 | 184.8 | 44.1 | 33.2
SCU-3 | RXYQ192PBTJ | 112 | 87.1 | 203866 | 8.0 / 50% | 151749 | 276 | 38.6 | 34.8
Name | Model | PS | MCA | MOP | Run Amps | St Curr | MOP | WxHxD | Wght
|  |  | A | A | A | A |  | inch | lbs
SCU-1 | RXYQ192PBTJ | %: 230V 3ph
| * RXYQ72PBTJ |  | 30 | 35 | 14.2 |  | 35A | 36.6x66.1x30.1 | 419
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
SCU-2 | RXYQ240PBTJ | %: 230V 3ph
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
SCU-3 | RXYQ192PBTJ | %: 230V 3ph
| * RXYQ72PBTJ |  | 30 | 35 | 14.2 |  | 35A | 36.6x66.1x30.1 | 419
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
Name | Ducted | Â°F: Non-ducted
| EER | IEER | COP 47Â°F | COP 17Â°F | EER | IEER | COP 47Â°F | COP 17Â°F
SCU-1 | 11.8 | 19.1 | 3.55 | 2.45 | 11.7 | 19.9 | 3.7 | 2.55
SCU-2 | 11.6 | 16.1 | 3.5 | 2.35 | 11.5 | 18.2 | 3.6 | 2.55
SCU-3 | 11.8 | 19.1 | 3.55 | 2.45 | 11.7 | 19.9 | 3.7 | 2.55

## Sheet1
| Name | FCU | Tmp C | TC | SC | Tmp H | HC |  | Suct | Disch | Airflow | Suct | Disch | Airflow | Sound | PS | MCA | MOP | WxHxD | Wght
1 | 101A BASEMENT:AC-1 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-1 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 201 B 3RD:AC-2 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-2 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 101A 2ND:AC-3 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-3 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 101B BASEMENT:AC-4 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-4 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 101B 1ST:AC-5 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-5 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 201A 2ND:AC-6 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-6 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 201A 2ND:AC-7 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-7 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 202A 2ND:AC-8 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-8 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 102A 1ST:AC-9 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-9 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 102B 1ST:AC-10 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-10 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 102B BASEMENT:AC-11 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-11 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 102A BASEMENT:AC-12 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-12 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 202A 2ND:AC-13 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-13 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 202B 2ND:AC-14 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-14 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 103B 1ST:AC-15 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-15 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 103A 1ST:AC-16 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-16 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 103 B BASEMENT:AC-17 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-17 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 103A BASEMENT:AC-18 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-18 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 203B 2ND:AC-19 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-19 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 203B 2ND:AC-20 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-20 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 104B 1ST:AC-21 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-21 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 104B 1ST:AC-22 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-22 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 203A 2ND:AC-23 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-23 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 104A 1ST:AC-24 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-24 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 203A 2ND:AC-25 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-25 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 104A 1ST:AC-26 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-26 | 64.4 | 81.4 | 260 | 68 | 85.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
1 | 1ST FL CORRIDOR WEST:C-1 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-1 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
1 | 2ND FLOOR CORRIDOR WEST:C-2 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-2 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
1 | 2ND FLR CORRIDOR CENTER WEST:C-5 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-5 | 64.4 | 88.7 | 290 | 68 | 93.2 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
TOTAL |  |  |  | 248436 | [12 empty] | 9
2 | 205 B 2ND:AC-27 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-27 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 105B 1ST:AC-28 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-28 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 205A 2ND:AC-29 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | AC-29 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 105A 1ST:AC-30 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | AC-30 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 106A BASEMENT:AC-31 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-31 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 106A AST:AC-32 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-32 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 204A 2ND:AC-33 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | AC-33 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 106A BASEMENT:AC-34 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-34 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 204B 2ND:AC-35 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-35 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 106B 1ST:AC-36 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-36 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 206B 2ND:AC-37 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-37 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 108B 1ST:AC-38 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-38 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 106B BASEMENT:AC-39 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-39 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 108B BASEMENT:AC-40 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-40 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 204A 3RD:AC-78 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-78 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 204A 3RD:AC-79 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100 | AC-79 | 64.4 | 82.1 | 280 | 68 | 86.3 | 280 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | BASEMENT CORRIDOR CTR EAST:C-6 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-6 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 2ND FL CORRIDOR CENTER EAST:C-7 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-7 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 205A 2ND:AC-41 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-41 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 105A 1ST:AC-42 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-42 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 207A 2ND:AC-43 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-43 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 107A 1ST:AC-44 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-44 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 207A 2ND:AC-45 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-45 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 207A 2ND:AC-46 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | AC-46 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 107 B 1ST:AC-47 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-47 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 207 B 2ND:AC-48 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-48 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 206A 2ND:AC-49 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | AC-49 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 108A 1ST:AC-50 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-50 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 108A BASEMENT:AC-51 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-51 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 108A BASEMENT:AC-52 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-52 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 206A 3RD:AC-81 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-81 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | 206A 3RD:AC-80 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-80 | 64.4 | 79.4 | 260 | 68 | 83.5 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
2 | BASSEMENT CORRIDOR CTR WES:C-3 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-3 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
2 | 1ST FLOOR CORRIDOR CTR WEST:C-4 | FXAQ12PVJU | 86.0 / 50% | 12846 | 9175 | 68 | 14000 | C-4 | 64.4 | 86 | 290 | 68 | 90.3 | 290 | 31-38 | 230V 1ph | 0.4 | 15A | 31.3x11.4x9.3 | 26
TOTAL |  |  |  | 319539 | [12 empty] | 11.1
3 | 110A BASEMENT:AC-61 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-61 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 110B 1ST:AC-62 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-62 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 110B 1ST:AC-63 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-63 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 110A 1ST:AC-64 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-64 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 209A 2ND:AC-65 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-65 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 110B BASEMENT:AC-66 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-66 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 111B BASEMENT:AC-67 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-67 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 111A BASEMENT:AC-68 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-68 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 111B 1ST:AC-69 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-69 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 209A 2ND:AC-70 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-70 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 111A BASEMENT:AC-71 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-71 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 209A 2ND:AC-72 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-72 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 209A 2ND:AC-73 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-73 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 112B 1ST:AC-74 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-74 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 210B 2ND:AC-75 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-75 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 112B BASEMENT:AC-76 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-76 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 112A 1ST:AC-77 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-77 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 208 A 2ND:AC-53 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-53 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 208A 2ND:AC-54 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100 | AC-54 | 64.4 | 85.7 | 280 | 68 | 90 | 280 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 208A 2ND:AC-55 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-55 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 109A AST:AC-56 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-56 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 2ND FL CORRIDOR EAST:C-9 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100 | C-9 | 64.4 | 85.7 | 280 | 68 | 90 | 280 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 1ST FL CORRIDOR EAST:C-10 | FXAQ09PVJU | 86.0 / 50% | 10173 | 7708 | 68 | 11100 | C-10 | 64.4 | 85.7 | 280 | 68 | 90 | 280 | 31-37 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 208 B 2ND:AC-57 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-57 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 208B 2ND:AC-58 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-58 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 109B 1ST:AC-59 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-59 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 109B 1ST:AC-60 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | AC-60 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
3 | 2ND FL CORRIDOE CTR EAST:C-8 | FXAQ07PVJU | 86.0 / 50% | 8073 | 6643 | 68 | 8700 | C-8 | 64.4 | 82.5 | 260 | 68 | 86.7 | 260 | 29-35 | 230V 1ph | 0.3 | 15A | 31.3x11.4x9.3 | 26
TOTAL |  |  |  | 232344 | [12 empty] | 8.4

## OUTDOOR UNIT SPECIFICATIONS
OUTDOOR UNIT SPECIFICATIONS
Name | Model | Comb | Tmp C | CC | Tmp H | HC | Piping | Bse Refr | Ex Refr
|  | % | Â°F | BTU/h | Â°F | BTU/h | ft | lbs | lbs
SCU-1 | RXYQ192PBTJ | 120 | 87.1 | 208604 | 8.0 / 50% | 152204 | 233.1 | 38.6 | 34.5
SCU-2 | RXYQ240PBTJ | 124 | 87.1 | 265227 | 8.0 / 50% | 173602 | 184.8 | 44.1 | 33.2
SCU-3 | RXYQ192PBTJ | 112 | 87.1 | 203866 | 8.0 / 50% | 151749 | 276 | 38.6 | 34.8
Name | Model | PS | MCA | MOP | Run Amps | St Curr | MOP | WxHxD | Wght
SCU-1 | RXYQ192PBTJ | %: 230V 3ph
| * RXYQ72PBTJ |  | 30 | 35 | 14.2 |  | 35A | 36.6x66.1x30.1 | 419
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
SCU-2 | RXYQ240PBTJ | %: 230V 3ph
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
SCU-3 | RXYQ192PBTJ | %: 230V 3ph
| * RXYQ72PBTJ |  | 30 | 35 | 14.2 |  | 35A | 36.6x66.1x30.1 | 419
| * RXYQ120PBTJ |  | 43 | 50 | 27.6 | 131 | 50A | 48.9x66.1x30.1 | 620
| EER | IEER | COP 47Â°F | COP 17Â°F | EER | IEER | COP 47Â°F | COP 17Â°F
SCU-1 | 11.8 | 19.1 | 3.55 | 2.45 | 11.7 | 19.9 | 3.7 | 2.55
SCU-2 | 11.6 | 16.1 | 3.5 | 2.35 | 11.5 | 18.2 | 3.6 | 2.55
SCU-3 | 11.8 | 19.1 | 3.55 | 2.45 | 11.7 | 19.9 | 3.7 | 2.55