| Prepared For: Dave Kelley | Date: April 29, 2016 Customer P.O. Number: S22434 Customer Project Number: |
| --- | --- |
| Sold To: AAA Energy | Job Number: Job Name: AAA Energy - Dave - Portland Housing |

Trane U.S. Inc. dba Trane is pleased to provide the enclosed submittal for your review and approval.

Product Summary

Qty	Product

1	Packaged Gas/Electric Rooftop Units

| Daniel Broderick Trane 860 Spring Street, Unit 1 Westbrook, ME 04092 Phone: (207) 828-1777 Cell: Fax: (207) 828-1511 | The attached information describes the equipment we propose to furnish for this project, and is submitted for your approval. |
| --- | --- |

Table Of Contents

Product Summary	1

Packaged Gas/Electric Rooftop Units (Item A1)	3

Tag Data	3

Product Data	4

Performance Data	4

Mechanical Specifications	6

Unit Dimensions	10

Weight, Clearance & Rigging Diagram	12

Accessory	14

Field Installed Options - Part/Order Number Summary	16

Packaged Gas/Electric Rooftop Units	16

Tag Data - Packaged Gas/Electric Rooftop Units (Qty: 1)

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| A1 | RTU-1 | 1 | 15 Ton VSD | YZD180F3RVB--DHA1C2B60000000000000000000 |

Product Data - Packaged Gas/Electric Rooftop Units

Item: A1  Qty: 1  Tag(s): RTU-1

Gas/Electric

Ultra high efficiency

Downflow

15 Ton

208-230/60/3

Reliatel

Gas Heat - Modulating

Economizer Dry Bulb 0-100% with barometric relief

VAV oversized motor w shaft ground ring

Hinged panels/Standard Filters

Standard condenser coil with hail guard

Through the base electric/gas

Unit Mounted Circuit Breaker

Powered convenience outlet

BACnet communications interface

Power exhaust (Fld)

Performance Data - Packaged Gas/Electric Rooftop Units

| Tags | RTU-1 |
| --- | --- |
| Design Airflow (cfm) | 6000 |
| Cooling Entering Dry Bulb (F) | 78.00 |
| Cooling Entering Wet Bulb (F) | 65.00 |
| Ent Air Rel Humidity (%) | 49.92 |
| Ambient Temp (F) | 95.00 |
| Cooling Leaving Unit DB (F) | 58.58 |
| Cooling Leaving Unit WB (F) | 56.19 |
| Gross Total Capacity (MBh) | 175.62 |
| Gross Sensible Capacity (MBh) | 142.64 |
| Gross Latent Capacity (MBh) | 32.98 |
| Net Total Capacity (MBh) | 161.39 |
| Net Sensible Capacity (MBh) | 128.41 |
| Net Sensible Heat Ratio (Number) | 0.80 |
| Heating EAT (F) | 50.00 |
| Heating LAT (F) | 93.01 |
| Heating Temp Rise (F) | 43.01 |
| Output Htg Capacity (MBh) | 280.00 |
| Output Htg Capacity w/Fan (MBh) | 294.23 |
| Design ESP (in H2O) | 1.750 |
| Component SP Add (in H2O) | 0.200 |
| Field Supplied Drive Kit Required | None |
| Indoor Mtr. Operating Power (bhp) | 4.52 |
| Indoor RPM (rpm) | 882 |
| Indoor Motor Power (kW) | 3.36 |
| Outdoor Motor Power (kW) | 0.78 |
| Compressor Power (kW) | 11.74 |
| System Power (kW) | 15.89 |
| IPLV @ AHRI (IPLV) | 0.0 |
| MCA (A) | 80.00 |
| MOP (A) | 90.00 |
| Compressor 1 RLA (A) | 15.90 |
| Compressor 2 RLA (A) | 15.90 |
| Condenser Fan FLA (A) | 5.30 |
| Evaporator Fan FLA (A) | 16.70 |
| Fan Motor Heat (MBh) | 14.23 |
| Evap Coil Leav Air Temp (DB) (F) | 55.99 |
| Evap Coil Leav Air Temp (WB) (F) | 55.15 |
| Dew Point Temp (F) | 54.59 |
| Rated capacity (AHRI) (MBh) | 172.00 |
| Exhaust fan power (kW) | 0.56 |
| Refrig charge (HFC-410A) - ckt 1 (lb) | 14.5 |
| Refrig charge (HFC-410A) - ckt 2 (lb) | 9.8 |
| ASHRAE 90.1 | Yes |
| Saturated Suction Temp Circuit 1 (F) | 51.38 |
| Saturated Discharge Temp Circuit 1 (F) | 116.40 |
| Saturated Suction Temp Circuit 2 (F) | 54.18 |
| Saturated Discharge Temp Circuit 2 (F) | 116.51 |
| Total Static Pressure (in H2O) | 1.950 |

Mechanical Specifications - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Modulating Gas Heat

The heating section shall have a drum and tube heat exchanger design using stainless steel components.  A variable speed forced combustion blower shall supply premixed fuel to a single burner ignited by a pilotless hot surface ignition system.  The leaving air temperature shall be communicated to the unit controls (ReliaTel) via a discharge air sensor.  This information along with the space temperature will be used to modulate the heating output.

In order to provide reliable operation, a pressure switch will require blower operation to initiate gas flow.

On an initial call for heat the combustion blower shall purge the heat exchanger 45 seconds before ignition.  The heat exchanger will operate at full fire initially and then modulate down to match the desired discharge air temperature.  After three unsuccessful ignition attempts, the entire heating system shall be locked out until manually reset.

Units shall be suitable for use with natural gas.

Tool-less Hail Guards

Tool-less, hail protection quality coil guards are available for condenser coil protection.

Hinged Access Doors

Sheet metal hinges are available on the Filter/Evaporator Access Door and the Compressor/Control Access Door. This option is available on all downflow models.

BACnet Communications

The BACnet communications interface allows the unit to communicate directly with a generic open protocol BACnet MS/TP Network Building Automation System Controls.

Accessory - Powered Exhaust

The powered exhaust shall provide exhaust of return air, when using an economizer, to maintain better building pressurization.

VAV Operation

The VFD shall receive a 0-10 Vdc signal from the unit controls based upon supply static pressure and shall cause the drive to accelerate or decelerate as required to maintain the supply static pressure setpoint. When subjected to high ambient return conditions the VFD shall reduce its output frequency to maintain operation.

General - Ultra High

The units shall be dedicated downflow or horizontal airflow. The operating range shall be between 125F and 0F in cooling as standard from the factory for all units. Cooling performance shall be rated in accordance with ARI testing procedures. All units shall be factory assembled, internally wired, fully charged with R-410A, and 100 percent run tested to check cooling operation, fan and blower rotation and control sequence, before leaving the factory. Wiring internal to the unit shall be colored and numbered for simplified identification. This product has been evaluated to Bi-National Standard CAN/CSA-C22.2 No. 236-05, UL 1995; and is eligible for CNL (Canadian National Standards Listed) and USL (United States Standards Listed).

Casing - Ultra High

Unit casing shall be constructed of zinc coated, heavy gauge, galvanized steel. Exterior surfaces shall be cleaned, phosphatized, and finished with a weather-resistant baked enamel finish. Unit's surface shall be tested 672 hours in a salt spray test in compliance with ASTM B117. Cabinet construction shall allow for all maintenance on one side of the unit. In order to ensure a water and air tight seal, service panels shall have lifting handles and no more than three screws to remove. All exposed vertical panels and top covers in the indoor air section shall be insulated with a 1/2-inch, 1-pound density foil-faced, fire-resistant, permanent, odorless, glass fiber material. The base of the downflow unit shall be insulated with 1/2-inch, 1-pound density foil-faced, closed-cell material. The downflow unit¿s base pan shall have no penetrations within the perimeter of the curb other than the raised 1 1/8-inch high supply/return openings to provide an added water integrity precaution,

if the condensate drain backs up. The base of the unit shall have provisions for forklift and crane lifting.

Compressors - Ultra High

The Trane eFlex  variable speed compressor shall be capable of speed modulation from 15Hz to a maximum of 75Hz. The minimum unit capacity shall be 25% of full load or less. The compressor motor shall be a permanent magnet type. Each variable speed compressor shall be matched with a specially designed, refrigerant-cooled, variable frequency drive which modulates the speed of the compressor motor and provides several compressor protection functions. Control of the variable speed compressor and inverter control, as well as tandem direct-drive, scroll type compressors, shall be integrated with the ReliaTel unit controller to ensure optimal equipment reliability and efficiency. Each ompressor shall have a crankcase heater installed, properly sized to minimize the amount of liquid refrigerant present in the oil sump during off cycles.

Controls - Ultra High

Unit shall be completely factory wired with necessary controls and contactor pressure lugs or terminal block for power wiring. Unit shall provide an external location for mounting a fused disconnect device. ReliaTel controls shall be provided for all 24-volt control functions. The resident control algorithms shall make all heating, cooling, and/or ventilating decisions in response to electronic signals from sensors measuring indoor and outdoor temperatures. The control algorithm maintains accurate temperature control, minimizes drift from set point, and provides better building comfort. A centralized control shall provide anti-short cycle timing and time delay between compressors to provide a higher level of machine protection.

Crankcase Heaters - Ultra High

These band heaters provide improved compressor reliability by warming the oil to prevent migration during off-cycles or low ambient conditions. These are standard on all Voyager models.

Discharge Line Thermostat - Ultra High

A bi-metal element discharge line thermostat is installed as a standard option on the discharge line of each system. This standard option provides extra protection to the compressors against high discharge temperatures in case of loss of charge, extremely high ambient and other conditions which could drive the discharge temperature higher. Discharge line thermostat is wired in series with high pressure control. When the discharge temperature rises above the protection limit, the bi-metal disc in the thermostat switches to the off position, opening the 24 Vac circuit. When the temperature on the discharge line cools down, the bi-metal disc closes the contactor circuit, providing power to the compressor. When the thermostat opens the fourth time, the ReliaTel control must be manually reset to resume operation on that stage.

Evaporator and Condenser Coils - Ultra High

Microchannel coils will be burst tested by the manufacturer. Internally finned, 5/16¿ copper tubes mechanically bonded to a configured aluminum plate fin shall be standard for evaporator coils. Microchannel condenser coils shall be standard on all units. Coils shall be leak tested to ensure the pressure integrity. The evaporator coil and condenser coil shall be leak tested to 225 psig and pressure tested to 450 psig. Sloped condensate drain pans are standard.

Filters - Ultra High

Two inch standard filters shall be factory supplied on all units. Optional MERV 8 or MERV 13 filters with filter removal tool shall be available.

Gas Heating Section - Ultra High

The heating section shall have a drum and tube heat exchanger design using corrosion resistant steel components. A forced combustion blower shall supply premixed fuel to a single burner ignited by a pilotless hot surface ignition system. In order to provide reliable operation, a negative pressure gas valve shall be used on standard furnaces and a pressure switch on furnaces with modulating heat that requires blower operation to initiate gas flow. On an initial call for heat, the combustion blower shall purge the heat exchanger 45 seconds before ignition. After three unsuccessful ignition attempts, the entire heating system shall be locked out until manually reset at the thermostat. Units shall be suitable for use with natural gas or propane (field installed kit) and shall also comply with California requirements for low NOx emissions. The 12½- 17½ tons shall have two stage heating (Gas/Electric only).

Indoor Fan - Ultra High

Units above shall have belt driven, FC centrifugal fans with adjustable motor sheaves. Units with standard motors shall have an adjustable idler-arm assembly for quick-adjustment of fan belts and motor sheaves. All motors shall be thermally protected. Oversized motors shall be available for high static application. All indoor fan motors meet the U.S. Energy Policy Act of 1992 (EPACT).

Outdoor Fans - Ultra High

The outdoor fan shall be direct-drive, statically and dynamically balanced, draw-through in the vertical discharge position. The fan motor(s) shall be permanently lubricated and shall have bulletining thermal overload protection.

Phase Monitor - Ultra High

The Phase Monitor is a three-phase line monitor module that protects against phase loss, phase reversal and phase unbalance. It is intended to protect compressors from reverse rotation. It has an operating input voltage range of 190-600 Vac, and LED indicators for ON and FAULT. There are no field adjustments and the module will automatically reset from a fault condition.

Refrigerant Circuits - Ultra High

Each refrigerant circuit shall have thermostatic expansion devices, service pressure ports, and refrigerant line filter driers factory installed as standard. An area shall be provided for replacement suction line driers.

CO2 Sensor Wiring - Ultra High

The unit wiring for field installed C02 sensors. Factory-installed C02 sensor wiring saves time and ensures proper unit connections for the field installed C02 sensor kits.

High Short Circuit Current Rating - Ultra High

Unit shall be provided with electrical subsystem that will with stand fault currents up to 65kA (208/230, 460 VAC) compliant with UL 1995 and NEC 440.4 (B). Each compressor circuit and the indoor fan shall have dedicated overcurrent protection. Three phase motors shall be protected by Class J time delay fuses. Single phase motors shall be protected by Class CC time delay fuses. All transformers shall also be protected with Class CC time delay fuses. Contactors shall be din rail mounted.

Hinged Access Doors - Ultra High

Sheet metal hinges are available on the Filter/Evaporator Access Door and the Compressor/Control Access Door. This option is available on all downflow models.

Horizontal Side Access with Circuit Breaker - Ultra High

This option is a thermal magnetic, molded case, HACR Circuit Breaker with provisions for through the base electrical connections. The circuit breaker will be installed in a water tight enclosure in the unit with access through a swinging door. Factory wiring will be provided from the switch to the unit high voltage terminal block. The circuit breaker will provide overcurrent protection, be sized per NEC and UL guidelines, and be agency recognized by UL/CSA.

Powered or Unpowered Convenience Outlet - Ultra High

This option is a GFCI, 120V/15amp, 2-plug, convenience outlet, either powered or unpowered. When the convenience outlet is powered, a service receptacle disconnect will be available. The convenience outlet is powered from the line side of the disconnect or circuit breaker, and therefore will not be affected by the position of the disconnect or circuit breaker. This option can only be ordered when the Through the Base Electrical with either the Disconnect Switch, or Circuit Breaker, option is ordered. This option is available on all downflow models (Gas/Electric only).

Through the Base Electrical with Circuit Breaker - Ultra High

This option is a thermal magnetic, molded case, HACR Circuit Breaker with provisions for through the base electrical connections. The circuit breaker will be installed in a water tight enclosure in the unit with access through a swinging door. Factory wiring will be provided from the switch to the unit high voltage terminal block. The circuit breaker will provide overcurrent protection, be sized per NEC and UL guidelines, and be agency recognized by UL/CSA.

BACnet Communications Interface - Ultra High

This option shall be provided to allow the unit to communicate directly with a generic open protocol BACnet MS/TP Network Building Automation System Controls.

Barometric Relief - Ultra High

Designed to be used on downflow units, barometric relief is an unpowered means of relieving excess building pressure.

Economizer-Downflow - Ultra High

The assembly includes fully modulating 0-100% motor and dampers, barometric relief, minimum position setting, preset linkage, wiring harness with plug, fixed dry bulb and spring return actuator. The barometric relief damper shall be standard with the downflow economizer and shall provide a pressure operated damper that shall be gravity closing and shall prohibit entrance of outside air during the equipment ¿off¿ cycle. Solid state enthalpy and differential enthalpy control shall be field-installed.

Indoor Fan Motor Shaft Grounding Ring - Ultra High

Shaft grounding rings are used on all VFD driven motors to provide a conductive discharge path away from the motor bearings to ground. Bearing Protection Ring shall be maintenance free circumferential ring of conductive micro fibers that discharges voltages to ground.

Oversized Motors - Ultra High

Oversized motors shall be available for high static applications.

Tool-less Hail Guards - Ultra High

Tool-less, hail protection quality coil guards are available for condenser coil protection.

Powered Exhaust - Ultra High

The powered exhaust shall provide exhaust of return air, when using an economizer, to maintain better building pressurization.

Unit Dimensions - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Unit Dimensions - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Weight, Clearance & Rigging Diagram - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Weight, Clearance & Rigging Diagram - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Accessory - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Accessory - Packaged Gas/Electric Rooftop Units

Item: A1   Qty: 1   Tag(s): RTU-1

Field Installed Options - Part/Order Number Summary

This is a report to help you locate field installed options that arrive at the jobsite. This report provides part or order numbers for each field installed option, and references it to a specific product tag. It is NOT intended as a bill of material for the job.

Product Family - Packaged Gas/Electric Rooftop Units

| Item | Tag(s) | Qty | Description | Model Number |
| --- | --- | --- | --- | --- |
| A1 | RTU-1 | 1 | 15 Ton VSD | YZD180F3RVB--DHA1C2B60000000000000000000 |

| Field Installed Option Description | Part/Ordering Number |
| --- | --- |
| Power exhaust | BAYPWRX029B |

# Text boxes

Submittal

J:\JOBS\2\51436\4\Portland Housing - Submittal.doc