## Project
CONCRETE COMPRESSIVE STRENGTH TEST - ASTM C39
PROJECT INFORMATION
Project No.: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
E-Mail: | athibeault@une.edu
Attention: | Al Thebeault
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Mix Design
| Material | Type | Quantity
| Aggregate |  |  | lb
| Sand |  |  | lb
| Cement |  |  | lb
| Water |  |  | gal
| Air Entrain. |  |  | oz
| Water Reducer |  |  | oz
Retarder
Accelerator
Distribution:
Remarks:

## Data-Rpt
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.:
Location:
Placement Date:
Lab Rec'd Date:
Truck #:
Ticket #:
Technician:
Mix Designation:
Design Strength:
Supplier:
Slump (initial) |  | inches
Slump (placed) |  | inches |  | Admixture:
Air Content |  | %
Conc. Temp. |  | O F |  | Volume (yds): |  | c.y. of |  | total
Air Temp |  | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.:
Placement Date:
Lab Rec'd Date:
Location:
Technician:
Supplier:
Mix Designation:
Design Strength:
Slump (initial) |  | in.
Slump (placed) |  | in.
Air Content |  | %
Conc Temp. |  | oF
Air Temp. |  | oF
Volume (yds) |  | of
Admixture:
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
Average 28 Day (psi):
Remarks:
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: Technician's Initials:MS

## Summary
Project Name: |  | UNE College of Pharmacy | [6 empty] | Project Number: |  |  | 14063
Client: |  | University of New England | [6 empty] | Mix Designation: |  |  | 3/4" Aggregate
Supplier: |  | Dragon Products | [6 empty] | Design Strength: |  |  | 3000psi
Cylinder Set Number | Date Cast | Slump (inches) | Air Content (%) | Concrete Temp. 0F | 7 Day Result (psi) AVG. | 14 Day Result (psi) | 28 Day Result (psi) | 28 Day Result (psi) | 28 Day AVG. (psi) | Range | Design Strength (PSI) | 3 Test 28 Day Moving Ave. | 28 Day Running Average | LOCATION OF PLACEMENT
C1 | 2008-05-01 | 4.5 | 4 | 69 | 2660 |  | 4520 | 4470 | 4495 | 50 | 3000 | #VALUE! | 2247.5 | Line 4 from F to G Footing and Foundation Wall
C2 | 2008-05-14 | 3.75 | 5.5 | 69.2 | 3180 |  | 4910 | 4640 | 4775 | 270 | 3000 | #VALUE! | 3090 | Wall; Line 1, C.2 to Line G.2, Footing; From F4 to C4
C3 | 2008-05-14 | 5 | 5.7 | 71.2 | 2680 |  | 4490 | 4100 | 4295 | 390 | 3000 | 4521.6667 | 3391.25 | Wall: Line 1, C.5 to Line G.2, Footing; From F4 to C4
C4 | 2008-05-27 | 6 | 7.6 | 71 | 2350 |  | 3780 | 3580 | 3680 | 200 | 3000 | 4250 | 3449 | North Side Wall
C5 | 2008-05-27 | 6 | 7.5 | 71 | 2630 |  | 4080 | 3970 | 4025 | 110 | 3000 | 4000 | 3545 | West Side Wall
C6 | 2008-05-29 | 5 | 5.9 | 70 | 2740 |  | 4280 | 4140 | 4210 | 140 | 3000 | 3971.6667 | 3640 | Line 6 to A2 and Line G2 to G3
C7 | 2008-06-13 | 6 | 6 | 73 | 3370 |  | 4210 | 4140 | 4175 | 70 | 3000 | 4136.6667 | 3706.875 | Foundation Walls: Line 1 B.5-A, Line A 1-2; Pier at E-2, Stairwell A Footings
C8 | 2008-06-13 | 6 | 5.4 | 74 |  |  | 4410 | 4140 | 4275 | 270 | 3000 | 4220 | 3770 | Foundation Walls: Line 1 B.5-A, Line A 1-2, Stairwell A Footings, Pier at E-2
C9 | 2008-06-20 | 5 | 6 | 75 | 3790 |  | 4810 | 4690 | 4750 | 120 | 3000 | 4400 | 3868 | Elevator Pit Floor - Including Footing D-3 & C-3
C10 | 2008-07-03 | 6-3/4* | 4.5 | 82.5 | 2800 |  | 4080 | 3970 | 4025 | 110 | 3000 | 4350 | 3882.2727 | Wall line C5 to A3 and footing line A3, B3
C11 | 2008-07-10 | 5.5 | 5.5 | 85 | 3210 |  | 4800 | 4510 | 4655 | 290 | 3000 | 4476.6667 | 3946.6667 | Footing B2.4, Stair A Wall, Stair B Footing
C12 | 2008-07-18 | 5.75 | 4.8 | 87 | 3410 | [5 empty] | 3000 |  |  | Walls: A from 2 to 3 and 1' Walls Around Stairway
FOR ACCEPTABLE CONCRETE, ACI STATES THAT THE AVERAGE OF ALL SETS OF THREE CONSECUTIVE STRENGTH TESTS EQUAL OR EXCEED THE SPECIFIED STRENGTH, AND THAT NO INDIVIDUAL STRENGTH TEST (AVERAGE OF TWO CYLINDERS) FALLS BELOW THE SPECIFIED STRENGTH BY MORE THAN 500 PSI. Remarks: *Denotes slump after addition of superplasticizer.

## 14063-C13
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C13
Location: | South Area Footing
Placement Date: | 2008-07-31
Lab Rec'd Date: | 2008-08-01
Truck #: | 183
Ticket #: | 4530385
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 4 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 5.8 | %
Conc. Temp. | 85 | O F |  | Volume (yds): | 10.5 | c.y. of | 52.5 | total
Air Temp | 80 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C13a | 2008-08-07 | 7 | 6 | 12 | 27.69 | 141.0237 | 76.934 | 4 | AB
C13b | 2008-08-28 | 28
C13c | 2008-08-28 | 28
C13d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C13
Placement Date: | 2008-07-31
Lab Rec'd Date: | 2008-08-01
Location: | South Area Footing
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 4 | in.
Air Content | 5.8 | %
Conc Temp. | 85 | oF
Air Temp. | 80 | oF
Volume (yds) | 10.5 | of | 52.5
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C13a | 2008-08-07 | 7 | 4 | 141.0237 | 28.2744 | 76.934 | 2720
C13b | 2008-08-28 | 28
C13c | 2008-08-28 | 28
C13d
Average 28 Day (psi):
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 52.5 Technician's Initials:AB

## 14063-C12
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C12
Location: | Walls: A from 2 to 3 and 1' Walls Around Stairway
Placement Date: | 2008-07-18
Lab Rec'd Date: | 2008-07-19
Truck #: | 170
Ticket #: | 4530224
Technician: | F. Clark
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 5.75 | inches |  | Admixture: | Glenium 7500 (Mid-Range Water Reducer)
Air Content | 4.8 | %
Conc. Temp. | 87 | O F |  | Volume (yds): | 6.5 | c.y. of | 13 | total
Air Temp | 98 | O F
Water Added | 8 | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C12a | 2008-07-25 | 7 | 5.995 | 12 | 28.3 | 144.3709 | 96.203 | 6 | AB
C12b | 2008-08-15 | 28
C12c | 2008-08-15 | 28
C12d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C12
Placement Date: | 2008-07-18
Lab Rec'd Date: | 2008-07-19
Location: | Walls: A from 2 to 3 and 1' Walls Around Stairway
Technician: | F. Clark
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 5.75 | in.
Air Content | 4.8 | %
Conc Temp. | 87 | oF
Air Temp. | 98 | oF
Volume (yds) | 6.5 | of | 13
Admixture: | Glenium 7500 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C12a | 2008-07-25 | 7 | 6 | 144.3709 | 28.2273 | 96.203 | 3410
C12b | 2008-08-15 | 28
C12c | 2008-08-15 | 28
C12d
Average 28 Day (psi):
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 13 Technician's Initials:FC

## 14063-C11
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C11
Location: | Footing B2.4, Stair A Wall, Stair B Footing
Placement Date: | 2008-07-10
Lab Rec'd Date: | 2008-07-11
Truck #: | 176
Ticket #: | 4530074
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 5.5 | inches |  | Admixture:
Air Content | 5.5 | %
Conc. Temp. | 85 | O F |  | Volume (yds): | 8 | c.y. of | 8 | total
Air Temp | 80 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C11a | 2008-07-17 | 7 | 5.985 | 12 | 28.2 | 144.3419 | 90.294 | 6 | AB
C11b | 2008-08-07 | 28 | 6 | 12 | 28.08 | 143.0099 | 127.559 | 6 | AB
C11c | 2008-08-07 | 28 | 5.999 | 12 | 28.14 | 143.3633 | 135.533 | 6 | AB
C11d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C11
Placement Date: | 2008-07-10
Lab Rec'd Date: | 2008-07-11
Location: | Footing B2.4, Stair A Wall, Stair B Footing
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 5.5 | in.
Air Content | 5.5 | %
Conc Temp. | 85 | oF
Air Temp. | 80 | oF
Volume (yds) | 8 | of | 8
Admixture:
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C11a | 2008-07-17 | 7 | 6 | 144.3419 | 28.1332 | 90.294 | 3210
C11b | 2008-08-07 | 28 | 6 | 143.0099 | 28.2744 | 127.559 | 4510
C11c | 2008-08-07 | 28 | 6 | 143.3633 | 28.265 | 135.533 | 4800
C11d
| Average 28 Day (psi): |  |  | 4655
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 8 Technician's Initials:AB

## 14063-C10
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C10
Location: | Wall line C5 to A3 and footing line A3 and B3
Placement Date: | 2008-07-03
Lab Rec'd Date: | 2008-07-04
Truck #: | 176
Ticket #: | 4529908
Technician: | AB
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 6-3/4 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 4.5 | %
Conc. Temp. | 82.5 | O F |  | Volume (yds): | 10 | c.y. of | 70 | total
Air Temp | 75 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C10a | 2008-07-10 | 7 | 5.985 | 12 | 28.09 | 143.7789 | 78.913 | 4 | AB
C10b | 2008-07-31 | 28 | 6 | 12 | 28.17 | 143.4683 | 115.26 | 4 | AB
C10c | 2008-07-31 | 28 | 6 | 12 | 28.18 | 143.5192 | 112.235 | 6 | AB
C10d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C10
Placement Date: | 2008-07-03
Lab Rec'd Date: | 2008-07-04
Location: | Wall line C5 to A3 and footing line A3 and B3
Technician: | AB
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 6-3/4 | in.
Air Content | 4.5 | %
Conc Temp. | 82.5 | oF
Air Temp. | 75 | oF
Volume (yds) | 10 | of | 70
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C10a | 2008-07-10 | 7 | 4 | 143.7789 | 28.1332 | 78.913 | 2800
C10b | 2008-07-31 | 28 | 4 | 143.4683 | 28.2744 | 115.26 | 4080
C10c | 2008-07-31 | 28 | 6 | 143.5192 | 28.2744 | 112.235 | 3970
C10d
| Average 28 Day (psi): |  |  | 4025
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 70 Technician's Initials: AB

## 14063-C9
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C9
Location: | Elevator Pit Floor - Including Footing D-3 & C-3
Placement Date: | 2008-06-20
Lab Rec'd Date: | 2008-06-23
Truck #: | 160
Ticket #: | 4529668
Technician: | A. Lyons
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 5 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 6 | %
Conc. Temp. | 75 | O F |  | Volume (yds): | 10.5 | c.y. of | 31.5 | total
Air Temp | 80 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C9a | 2008-06-27 | 7 | 5.995 | 12 | 27.96 | 142.6364 | 107.117 | 4 | AB
C9b | 2008-07-18 | 28 | 6 | 12 | 28.63 | 145.8111 | 132.564 | 6 | AB
C9c | 2008-07-18 | 28 | 5.999 | 12 | 28.26 | 143.9746 | 135.872 | 4 | AB
C9d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C9
Placement Date: | 2008-06-20
Lab Rec'd Date: | 2008-06-23
Location: | Elevator Pit Floor - Including Footing D-3 & C-3
Technician: | A. Lyons
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 5 | in.
Air Content | 6 | %
Conc Temp. | 75 | oF
Air Temp. | 80 | oF
Volume (yds) | 10.5 | of | 31.5
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C9a | 2008-06-27 | 7 | 4 | 142.6364 | 28.2273 | 107.117 | 3790
C9b | 2008-07-18 | 28 | 6 | 145.8111 | 28.2744 | 132.564 | 4690
C9c | 2008-07-18 | 28 | 4 | 143.9746 | 28.265 | 135.872 | 4810
C9d
| Average 28 Day (psi): |  |  | 4750
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 31.5 Technician's Initials:AL

## 14063-C8
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C8
Location: | Foundation Walls: Line 1 B.5-A, Line A 1-2
Stairwell A Footings, Pier at E-2
Placement Date: | 2008-06-13
Lab Rec'd Date: | 2008-06-14
Truck #: | 189
Ticket #: | 4529555
Technician: | A. Lyons
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 6 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 5.4 | %
Conc. Temp. | 74 | O F |  | Volume (yds): | 61.5 | c.y. of | 71.5 | total
Air Temp | 83 | O F
Water Added | 20 | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C8a | 2008-06-20 | 7 | 5.999 | 12 | 28.37 | 144.5351 | 114.285 | 6 | AB
C8b | 2008-07-11 | 28 | 6 | 12 | 28.5 | 145.149 | 117.14 | 6 | AB
C8c | 2008-07-11 | 28 | 5.995 | 12 | 28.35 | 144.626 | 124.506 | 6 | AB
C8d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C8
Placement Date: | 2008-06-13
Lab Rec'd Date: | 2008-06-14
Location: | Foundation Walls: Line 1 B.5-A, Line A 1-2
Stairwell A Footings, Pier at E-2
Technician: | A. Lyons
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 6 | in.
Air Content | 5.4 | %
Conc Temp. | 74 | oF
Air Temp. | 83 | oF
Volume (yds) | 61.5 | of | 71.5
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C8a | 2008-06-20 | 7 | 6 | 144.5351 | 28.265 | 114.285 | 4040
C8b | 2008-07-11 | 28 | 6 | 145.149 | 28.2744 | 117.14 | 4140
C8c | 2008-07-11 | 28 | 6 | 144.626 | 28.2273 | 124.506 | 4410
C8d
| Average 28 Day (psi): |  |  | 4275
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 71.5 Technician's Initials:AL

## 14063-C7
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C7
Location: | Foundation Walls: Line 1 B.5 - A, Line A 1-2
Pier at E - 2, Stairwell A Footings
Placement Date: | 2008-06-13
Lab Rec'd Date: | 2008-06-14
Truck #: | 189
Ticket #: | 4529547
Technician: | A. Lyons
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 6 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 6 | %
Conc. Temp. | 73 | O F |  | Volume (yds): | 21 | c.y. of | 71.5 | total
Air Temp | 77.5 | O F
Water Added | 15 | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C7a | 2008-06-20 | 7 | 5.995 | 12 | 28.27 | 144.2179 | 95.086 | 6 | AB
C7b | 2008-07-11 | 28 | 5.999 | 12 | 28.3 | 144.1784 | 117.07 | 6 | AB
C7c | 2008-07-11 | 28 | 6 | 12 | 28.45 | 144.8943 | 119.12 | 6 | AB
C7d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C7
Placement Date: | 2008-06-13
Lab Rec'd Date: | 2008-06-14
Location: | Foundation Walls: Line 1 B.5 - A, Line A 1-2
Pier at E - 2, Stairwell A Footings
Technician: | A. Lyons
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 6 | in.
Air Content | 6 | %
Conc Temp. | 73 | oF
Air Temp. | 77.5 | oF
Volume (yds) | 21 | of | 71.5
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C7a | 2008-06-20 | 7 | 6 | 144.2179 | 28.2273 | 95.086 | 3370
C7b | 2008-07-11 | 28 | 6 | 144.1784 | 28.265 | 117.07 | 4140
C7c | 2008-07-11 | 28 | 6 | 144.8943 | 28.2744 | 119.12 | 4210
C7d
| Average 28 Day (psi): |  |  | 4175
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 71.5 Technician's Initials:AL

## 14063-C6
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C6
Location: | Line C to A2 and Line G2 to G3
Placement Date: | 2008-05-29
Lab Rec'd Date: | 2008-05-30
Truck #: | 192
Ticket #: | 4529251
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 5 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 5.9 | %
Conc. Temp. | 68.1 | O F |  | Volume (yds): | 8.5 | c.y. of | 17 | total
Air Temp | 70.8 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C6a | 2008-06-05 | 7 | 6 | 12 | 27.74 | 141.2783 | 77.415 | 5 | AB
C6b | 2008-06-26 | 28 | 5.99 | 12 | 27.79 | 142.0059 | 116.73 | 6 | AB
C6c | 2008-06-26 | 28 | 5.995 | 12 | 27.65 | 141.055 | 120.774 | 6 | AB
C6d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C6
Placement Date: | 2008-05-29
Lab Rec'd Date: | 2008-05-30
Location: | Line C to A2 and Line G2 to G3
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 5 | in.
Air Content | 5.9 | %
Conc Temp. | 68.1 | oF
Air Temp. | 70.8 | oF
Volume (yds) | 8.5 | of | 17
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C6a | 2008-06-05 | 7 | 5 | 141.2783 | 28.2744 | 77.415 | 2740
C6b | 2008-06-26 | 28 | 6 | 142 | 28.1802 | 116.73 | 4140
C6c | 2008-06-26 | 28 | 6 | 141 | 28.2273 | 120.774 | 4280
C6d
| Average 28 Day (psi): |  |  | 4210
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 17 Technician's Initials:AB

## 14063-C5
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C5
Location: | West Side Wall
Placement Date: | 2008-05-27
Lab Rec'd Date: | 2008-05-28
Truck #: | 183
Ticket #: | 4529213
Technician: | M. Sullivan
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 6 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 7.5 | %
Conc. Temp. | 71 | O F |  | Volume (yds): | 70 | c.y. of | 87 | total
Air Temp | 80 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C5a | 2008-06-03 | 7 | 5.995 | 12 | 27.81 | 141.8712 | 74.333 | 6 | AB
C5b | 2008-06-24 | 28 | 5.985 | 12 | 27.73 | 141.9362 | 114.794 | 6 | AB
C5c | 2008-06-24 | 28 | 5.999 | 12 | 27.9 | 142.1406 | 112.107 | 6 | AB
C5d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C5
Placement Date: | 2008-05-27
Lab Rec'd Date: | 2008-05-28
Location: | West Side Wall
Technician: | M. Sullivan
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 6 | in.
Air Content | 7.5 | %
Conc Temp. | 71 | oF
Air Temp. | 80 | oF
Volume (yds) | 70 | of | 87
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C5a | 2008-06-03 | 7 | 6 | 141.8712 | 28.2273 | 74.333 | 2630
C5b | 2008-06-24 | 28 | 6 | 141.9362 | 28.1332 | 114.794 | 4080
C5c | 2008-06-24 | 28 | 6 | 142.1406 | 28.265 | 112.107 | 3970
C5d
| Average 28 Day (psi): |  |  | 4025
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 87 Technician's Initials:MS

## 14063-C4
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C4
Location: | North Side Wall
Placement Date: | 2008-05-27
Lab Rec'd Date: | 2008-05-28
Truck #: | 175
Ticket #: | 4529209
Technician: | M. Sullivan
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 6 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 7.6 | %
Conc. Temp. | 71 | O F |  | Volume (yds): | 30 | c.y. of | 87 | total
Air Temp | 80 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C4a | 2008-06-03 | 7 | 6 | 12 | 26.79 | 136.44 | 66.402 | 6 | SB
C4b | 2008-06-24 | 28 | 5.995 | 12 | 26.61 | 135.7495 | 101.066 | 6 | AB
C4c | 2008-06-24 | 28 | 5.997 | 12 | 26.65 | 135.8628 | 106.863 | 6 | AB
C4d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C4
Placement Date: | 2008-05-27
Lab Rec'd Date: | 2008-05-28
Location: | North Side Wall
Technician: | M. Sullivan
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 6 | in.
Air Content | 7.6 | %
Conc Temp. | 71 | oF
Air Temp. | 80 | oF
Volume (yds) | 30 | of | 87
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C4a | 2008-06-03 | 7 | 6 | 136.44 | 28.2744 | 66.402 | 2350
C4b | 2008-06-24 | 28 | 6 | 135.7495 | 28.2273 | 101.066 | 3580
C4c | 2008-06-24 | 28 | 6 | 135.8628 | 28.2461 | 106.863 | 3780
C4d
| Average 28 Day (psi): |  |  | 3680
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 87 Technician's Initials:MS

## 14063-C3
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C3
Location: | Wall; Line 1, C.5 to Line G.2
Footing; From F4 to C4
Placement Date: | 2008-05-14
Lab Rec'd Date: | 2008-05-15
Truck #: | 170
Ticket #: | 4579001
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 5 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 5.7 | %
Conc. Temp. | 71.2 | O F |  | Volume (yds): | 10 | c.y. of | 100 | total
Air Temp | 72.8 | O F
Water Added | 25 | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C3a | 2008-05-21 | 7 | 5.99 | 12 | 28.08 | 143.4878 | 75.605 | 5 | AB
C3b | 2008-06-11 | 28 | 5.995 | 12 | 28.12 | 143.4526 | 126.626 | 4 | AB
C3c | 2008-06-11 | 28 | 5.985 | 12 | 28.04 | 143.5229 | 115.458 | 6 | AB
C3d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C3
Placement Date: | 2008-05-14
Lab Rec'd Date: | 2008-05-15
Location: | Wall; Line 1, C.5 to Line G.2
Footing; From F4 to C4
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 5 | in.
Air Content | 5.7 | %
Conc Temp. | 71.2 | oF
Air Temp. | 72.8 | oF
Volume (yds) | 10 | of | 100
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C3a | 2008-05-21 | 7 | 5 | 143.4878 | 28.1802 | 75.605 | 2680
C3b | 2008-06-11 | 28 | 4 | 143.4526 | 28.2273 | 126.626 | 4490
C3c | 2008-06-11 | 28 | 6 | 143.5229 | 28.1332 | 115.458 | 4100
C3d
| Average 28 Day (psi): |  |  | 4295
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 100 Technician's Initials:AB

## 14063-C2
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C2
Location: | Wall; Line 1, C.2 to Line G.2
Footing; From F4 to C4
Placement Date: | 2008-05-14
Lab Rec'd Date: | 2008-05-15
Truck #: | 190
Ticket #: | 4528994
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 3.75 | inches |  | Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Air Content | 5.5 | %
Conc. Temp. | 69.2 | O F |  | Volume (yds): | 10 | c.y. of | 100 | total
Air Temp | 73.5 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C2a | 2008-05-21 | 7 | 5.995 | 12 | 28.2 | 143.8608 | 89.799 | 5 | AB
C2b | 2008-06-11 | 28 | 5.99 | 12 | 28.12 | 143.6922 | 138.459 | 6 | AB
C2c | 2008-06-11 | 28 | 6 | 12 | 28.21 | 143.672 | 131.334 | 6 | AB
C2d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C2
Placement Date: | 2008-05-14
Lab Rec'd Date: | 2008-05-15
Location: | Wall; Line 1, C.2 to Line G.2
Footing; From F4 to C4
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 3.75 | in.
Air Content | 5.5 | %
Conc Temp. | 69.2 | oF
Air Temp. | 73.5 | oF
Volume (yds) | 10 | of | 100
Admixture: | Polyheed 997 (Mid-Range Water Reducer)
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C2a | 2008-05-21 | 7 | 5 | 143.8608 | 28.2273 | 89.799 | 3180
C2b | 2008-06-11 | 28 | 6 | 143.6922 | 28.1802 | 138.459 | 4910
C2c | 2008-06-11 | 28 | 6 | 143.672 | 28.2744 | 131.334 | 4640
C2d
| Average 28 Day (psi): |  |  | 4775
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 100 Technician's Initials:AB

## 14063-C1
CONCRETE COMPRESSIVE STRENGTH TEST DATA - ASTM C39
TEST DATA
Project No: | 14063
Project: | UNE College of Pharmacy
Set No.: | C1
Location: | Line 4 from F to G Footing and Foundation Wall
Placement Date: | 2008-05-01
Lab Rec'd Date: | 2008-05-02
Truck #: | 176
Ticket #: | 3930234
Technician: | A. Boubacar
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Supplier: | Dragon Products
Slump (initial) |  | inches
Slump (placed) | 4.5 | inches |  | Admixture:
Air Content | 4 | %
Conc. Temp. | 69.6 | O F |  | Volume (yds): | 10 | c.y. of | 46.5 | total
Air Temp | 49.8 | O F
Water Added |  | Gals
TEST DATA
Sample No. | Test Date | Age | Dia (in) | Length (in) | Weight (lb) | Unit Weight | Load (k) | Type | Tech
C1a | 2008-05-08 | 7 | 5.988 | 12 | 28.13 | 143.8394 | 74.799 | 6 | RM
C1b | 2008-05-29 | 28 | 5.995 | 12 | 28.21 | 143.9118 | 126.132 | 6 | AB
C1c | 2008-05-29 | 28 | 5.99 | 12 | 28.17 | 143.9477 | 127.446 | 6 | AB
C1d
CONCRETE COMPRESSIVE STRENGTH TEST RESULTS - ASTM C39
Project No: | 14063
Project: | UNE College of Pharmacy
Client: | University of New England
11 Hills Beach Road
Biddeford, Maine 04005
Field Test Data
Set No.: | C1
Placement Date: | 2008-05-01
Lab Rec'd Date: | 2008-05-02
Location: | Line 4 from F to G Footing and Foundation Wall
Technician: | A. Boubacar
Supplier: | Dragon Products
Mix Designation: | 3/4" Aggregate
Design Strength: | 3000psi
Slump (initial) |  | in.
Slump (placed) | 4.5 | in.
Air Content | 4 | %
Conc Temp. | 69.6 | oF
Air Temp. | 49.8 | oF
Volume (yds) | 10 | of | 46.5
Admixture:
Laboratory Test Data
Sample No. | Test Date | Age | Type | Unit Wt. | Area (in2) | Load (K) | Strength (psi)
C1a | 2008-05-08 | 7 | 6 | 143.8394 | 28.1614 | 74.799 | 2660
C1b | 2008-05-29 | 28 | 6 | 143.9118 | 28.2273 | 126.132 | 4470
C1c | 2008-05-29 | 28 | 6 | 143.9477 | 28.1802 | 127.446 | 4520
C1d
| Average 28 Day (psi): |  |  | 4495
Remarks:
Formulas:
Test Date = IF(ISBLANK([inches]),"",B11+[inches])
3
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
5
1
2
4
3
6
Cone
Cone and Split
Cone and Shear
Shear
Columnar
Other
Have cylinders been logged into computer? Yes: X No: Curebox Temp. Min.: Max.: Total Yards: 46.5 Technician's Initials:MS