Copyright 1998, The American Institute of Architects (AIA)

SECTION 05310 - STEEL DECK

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

Adjust list below to suit Project.

          - Roof deck.

        - Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

          - Division 5 Section "Structural Steel" for shop-welded shear connectors.

          - Division 5 Section "Metal Fabrications" for framing deck openings with miscellaneous steel shapes.

      - SUBMITTALS

        - Product Data:  For each type of deck, accessory, and product indicated.

        - Shop Drawings:  Show layout and types of deck panels, anchorage details, reinforcing channels, pans, deck openings, special jointing, accessories, and attachments to other construction.

Retain paragraph below if required.

        - Product Certificates:  Signed by steel deck manufacturers certifying that products furnished comply with requirements.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

        - Welding Certificates:  Copies of certificates for welding procedures and personnel.

Delete paragraph and subparagraphs below if not required.  List other product test reports if required.

Insert specific model code organization below or revise if report must be from another source.

      - QUALITY ASSURANCE

        - Installer Qualifications:  An experienced installer who has completed steel deck similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

Delete paragraph below if test reports from qualified testing agencies are not required.  Retain and coordinate with "Field Quality Control" Article if Contractor or manufacturer selects testing agency.

Delete paragraph below if not using cellular deck floor systems as raceways.

Delete paragraph below if no welding.  Retain "Welding Certificates" Paragraph in "Submittals" Article if below is retained.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

        - Welding:  Qualify procedures and personnel according to AWS D1.1, "Structural Welding Code--Steel," and AWS D1.3, "Structural Welding Code--Sheet Steel."

Delete paragraph below if no fire-resistance-rated steel deck units are required.

        - AISI Specifications:  Calculate structural characteristics of steel deck according to AISI's "Specification for the Design of Cold-Formed Steel Structural Members."

Delete paragraph below if not using cellular deck floor systems as raceways.

Delete below if FM compliance is not required for roof deck.  Seven manufacturers have products listed in FM's "Approval Guide, Building Materials."

        - FM Listing:  Provide steel roof deck evaluated by FM and listed in FM's "Approval Guide, Building Materials" for Class 1 fire rating and Class 1-90 windstorm ratings.

      - DELIVERY, STORAGE, AND HANDLING

        - Protect steel deck from corrosion, deformation, and other damage during delivery, storage, and handling.

        - Stack steel deck on platforms or pallets and slope to provide drainage.  Protect with a waterproof covering and ventilate to avoid condensation.

      - PROJECT CONDITIONS

        - Design:

          - Steel deck shall be designed in accordance with the AISI "Specifications for the Design of Cold-Formed Steel Structural Members."  Simple short spans shall be avoided, and all deck units shall extend over three or more supports unless absolutely impractical.

          - Design Loads:  As specified on the drawings.

      - COORDINATION

Retain paragraph below if acoustical insulation is specified in this Section to be placed in topside ribs.  Revise if site installation of sound-absorbing insulation in cells of cellular acoustical deck is specified.

        - Coordinate installation of sound-absorbing insulation strips in topside ribs of acoustical deck with roofing installation specified in Division 7 Section 07531 E.P.D.M. MEMBRANE ROOFING to ensure protection of insulation strips against damage from effects of weather and other causes.

- PRODUCTS

      - ROOF DECK

Paragraph 2.2: Materials and Subparagraphs are from Allieds Master Spec. Use as a guide to edit Paragraph 2.3: Roof Deck as required

        - Steel Acoustic Roof Deck (1-1/2"):  Provide painted steel acoustic roof deck with 1-1/2" batt insulation and all necessary accessories conforming to ASTM A 611, Grade C.  Steel deck shall be 22 gauge with all required accessories for a complete and finished installation.  Accessories to be of the same material as the deck unless otherwise specified.  Metal deck shall be Type BA, Test A76-125 with 1-1/2" batt insulation by United Steel Deck, Inc., or approved equal.  (At areas where metal deck is scheduled to receive a finish top coating, verify compatibility of primer.)

      - ACCESSORIES

        - General:  Provide manufacturer's standard accessory materials for deck that comply with requirements indicated.

        - Adjusting Plates:  Provide adjusting plates or segments of roof units in locations too narrow to accommodate full-size roof units.  As far as practical, provide plates of the same gauge and configuration as the roof units.  Plates of predetermined sizes shall be factory cut.

        - Reinforcing Plates:  Provide .057” thick reinforcing plates for all openings less than 12 inches in diameter. Length and width of plates as required satisfying The Steel Deck Institute requirements.

        - Mechanical Fasteners:  Corrosion-resistant, low-velocity, power-actuated or pneumatically driven carbon-steel fasteners equal to Hilti equal to Hilti X-EDNI19-THQ12-HSN; or # 12 or larger self-drilling, self-threading screws.

        - Side-Lap Fasteners:  Corrosion-resistant, hexagonal washer head; self-drilling, carbon-steel screws, No. 12 minimum diameter.

        - Flexible Closure Strips:  Vulcanized, closed-cell, synthetic rubber.

        - Miscellaneous Sheet Metal Deck Accessories:  Steel sheet, minimum yield strength of 33,000 psi, not less than 0.0359-inch design uncoated thickness, of same material and finish as deck; of profile indicated or required for application.

        - Steel Sheet Accessories:  Steel sheet, of same material, finish, and thickness as deck, unless otherwise indicated.

        - End Closures:  Provide end closures of minimum 22 gauge to close the ends at end walls, eaves, and openings through the roof.

Pour stop thickness and profile guidance are presented in SDI Publication No. 29.  Revise paragraph below to suit Project.

Piercing hanger tabs below are designed for embedment in deck slab; delete if not permitted or required.  SDI advises against using roof deck to support suspended ceilings, light fixtures, ducts, or utilities.  Rolled-in hanger tabs are available for floor deck but improper use could result in overstressing the tabs or overloading the deck slab.  If allowed, insert rolled-in hanger tabs here; verify load limits, availability, limitations, and recommendations with deck manufacturers.

Usually retain weld washers below if weld-fastening deck with an uncoated minimum steel thickness of less than 0.028 inch 0.71 mm.  Select weld washer thickness.

        - Weld Washers:  Uncoated steel sheet, shaped to fit deck rib, thickness as required by manufacturer.

Retain paragraph above or below if required.  Select level or sloped sump pans.  Recessed sump pans are seldom used.  Coordinate with choice of roof drain if recessed sump pans are required.  Delete above and retain below if flat sump plates are required.

- EXECUTION

      - EXAMINATION

        - Examine supporting frame and field conditions for compliance with requirements for installation tolerances and other conditions affecting performance.

      - INSTALLATION, GENERAL

        - Install deck panels and accessories according to applicable specifications and commentary in SDI Publication No. 29, manufacturer's written instructions, and requirements in this Section.

        - Locate decking bundles to prevent overloading of supporting members.

          - Exercise special care not to damage the material or overload the decking during the entire construction period.  The maximum uniform distribution storage load shall not exceed the design live load.

        - Place deck panels on supporting frame and adjust to final position with ends accurately aligned and bearing on supporting frame before being permanently fastened.  Do not stretch or contract side-lap interlocks.

          - Simple short spans shall be avoided, and all deck units shall extend over three or more supports unless absolutely impractical.  Do not use unanchored deck units as a work or storage platform.

Retain subparagraph below if either long-span cellular roof deck or cellular floor deck with electrical distribution is required.

        - Place deck panels flat and square and fasten to supporting frame without warp or deflection.

        - Cut and neatly fit deck panels and accessories around openings and other work projecting through or adjacent to decking. Reinforce and frame openings through roof in accordance with the drawings for rigidity and load-carrying capacity.  Holes or other openings required for the work of other trades shall be drilled or cut and reinforced by the respective trades; the deck manufacturer and the Engineer shall approve such holes or other openings larger than 6 inches in diameter.

Coordinate reinforcing requirements of openings in paragraph below with other Division 5 Sections.

        - Provide additional reinforcement and closure pieces at openings as required for strength, continuity of decking, and support of other work.

        - Comply with AWS requirements and procedures for manual shielded metal arc welding, appearance and quality of welds, and methods used for correcting welding work.

Retain below if mechanical fastening is permitted.

        - Mechanical fasteners may be used in lieu of welding to fasten deck.  Locate mechanical fasteners and install according to deck manufacturer's written instructions.

      - DECK INSTALLATION

This Article includes installation requirements for classes of roof deck and form deck used in roof applications.  Revise paragraph below and insert requirements if mechanical fastening to supports will be permitted.

        - Immediately after placement and alignment, and after inaccuracies have been corrected, permanently fasten steel roof deck and floor deck units in place.  Clamp or weight deck units to provide firm contact between deck units and structural supports while fastening is being performed.  Decking shall be fastened as recommended by the manufacturer unless indicated otherwise on the drawings.

SDI requires side-lap and perimeter edge fastening if deck spans exceed 60 inches (1524 mm).  Revise fastener spacing if required.

Retain acceptable fastening method(s) from subparagraphs below.  Coordinate with choice of side lap.

          - Mechanically fasten with self-drilling No. 12 diameter or larger carbon-steel screws.

FM accepts welding of side laps to deck that is a minimum of 0.0474 inch (1.20 mm) thick.

        - End Bearing:  Install deck ends over supporting frame as per drawings or unless otherwise noted, with a minimum end bearing of 1-1/2 inches, with end joints as follows:

Select one of three options in subparagraph below.  SDI permits lapped or butted ends to roof deck.  FM recommends ends lap a minimum of 2 inches (51 mm).

          - End Joints:  Lapped 2 inches minimum

        - Miscellaneous Roof Deck Accessories: finish strips, cover plates, end closures, and reinforcing channels according to deck manufacturer's written instructions.  Weld to substrate to provide a complete deck installation.

Delete paragraph below if flexible closures are not required or permitted.  Usually delete if fire-resistance-rated partitions are required.

Retain below if installation of sound-absorbing insulation is specified in applicable low-slope roofing Section.  Coordinate with roofing installation to prevent exposure to weather.

      - FIELD QUALITY CONTROL

        - Inspect the decking top surface for flatness after installation.  Place a four-foot straightedge across the decking ribs over the structural supporting members at all locations.  If the straightedge fails to touch the entire top surface of the decking or if top surfaces of abutting units are not in alignment, corrective measures or replacement shall be provided.  After corrective measures or replacement has been performed, the decking shall be reinspected.

Retain this Article if field inspection and testing are required.  Revise paragraph below if Contractor engages agency.

        - Field welds will be subject to inspection.

Retain paragraph and subparagraphs below if shear connector studs are required.

        - Testing agency will report test results promptly and in writing to Contractor and Engineer.

        - Remove and replace work that does not comply with specified requirements.

      - REPAIRS AND PROTECTION

Retain one or more of three paragraphs below if repairs to galvanized or painted surfaces will be required.  If limiting repairs to roof deck, revise paragraphs accordingly.

Usually retain paragraph below for prime-painted deck and select surface(s) requiring repair painting.  Since shop primer protects for a limited time, repair painting is best applied during or immediately after deck installation.

        - Repair Painting:  Wire brush and clean rust spots, welds, and abraded areas on both surfaces of prime-painted deck immediately after installation, and apply repair paint.

Retain one of two subparagraphs below if appearance is important.  Retain first subparagraph with "both surfaces" option in paragraph above.  Retain second subparagraph if preparation and repair painting of bottom surface are specified in a Division 9 Section.

Delete paragraph and two subparagraphs above and retain paragraph below if repair painting requirements are included in Division 9.  Coordinate field painting requirements with applicable Division 9 Section.

        - Provide final protection and maintain conditions to ensure that steel deck is without damage or deterioration at time of Substantial Completion.

END OF SECTION 05310