Copyright 1998, The American Institute of Architects (AIA)

SECTION 13280 – HAZARDOUS MATERIAL REMEDIATION

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

      - SECTION INCLUDES

        - Furnish all labor, materials, equipment, supplies, and perform all operations necessary to complete the Design, removal, encapsulation and or enclosure of asbestos-containing building materials (ACBM) by competent persons trained, knowledgeable and qualified in the techniques of asbestos abatement, handling and disposal of asbestos-containing building materials and asbestos-contaminated materials and the subsequent cleaning of contaminated areas, complying with all applicable federal, state, and local regulations in accordance with the drawings and these specifications.

        - Work contemplated will be the removal of asbestos-containing building materials where shown on the drawings or as identified in part 3 of this section.

        - Lead Coatings have been found in this facility and are identified in part 3 of this section.  It shall be the responsibility of the contractor to follow all State and Federal regulations for the Design, removal and disposal of lead coated materials as required for demolition, cutting and welding ,of existing steel members, including all TCLP testing of materials prior to disposal.

      - QUALITY ASSURANCE

        - Job Site References:  Have on the job site at all times at least one copy of the following:

          - Plans and Specifications

          - Federal Register - Part II, Department of Labor - OSHA - 29 CFR Parts 1910.1001 and 1926.1101

          - Maine Department of Environmental Protection - Rules and Regulations Chapter 425.

          - Federal Register - Part II, Department of Labor - OSHA - 29 CFR Parts 1926.62 and

        - Medical Requirements:  29 CFR 1910.1001 and 1926.1101

          - Medical Questionnaires:  Administer medical questionnaires in accordance with 29 CFR 1910.1001-Appendix D and 29 CFR 1926.1101-Appendix D.

          - Medical Examinations:  Provide workers with a comprehensive medical examination as required by 29 CFR 1910.1001 and 1926.1101.  The same medical examination shall be given on an annual basis to employees engaged in an occupation involving potential exposure to asbestos fibers and within 30 calendar days before or after the termination of employment in such occupation.  Specifically identify X-ray films of asbestos workers to the consulting radiologist and mark medical record jackets with the word "ASBESTOS."

          - Medical Records:  Maintain complete and accurate records of employee's medical examinations for a period of 30 years after termination of employment and make records of the required medical examinations available for inspection and copy to:  The Assistant Secretary of Labor for Occupational Safety and Health, The Director of the National Institute for Occupational Safety and Health (NIOSH), authorized representatives of either of them, and an employee's physician upon the request of the employee or former employee.

        - Medical Surveillance for Lead workers:  29 CFR 1910.1025 and 1926.62 shall include, but not be limited to, the following:

          - Initial medical surveillance to include:

            - Blood sampling and analysis for lead and zinc protoporphyrin levels.

          - Continuing medical surveillance program for all employees who are or may be exposed at work at or above the action level for more than 30 days in any consecutive 12-month period.

            - All medical exams and procedures shall be performed by or under the supervision of a licensed physician and as detailed in 29 CFR 1926.62.

            - All medical surveillance shall be at no cost to the employees.

          - Administrative controls to reduce employee's exposure.

          - All Contractor's within the scope of lead abatement shall be required to have a written medical surveillance plan.  Minimum shall be as stated above

        - Training Requirements:

          - Asbestos Workers:  All workers must receive a three-day training course from an EPA or DEP accredited program and pass an examination with a minimum of 70% score.

          - Asbestos Competent Person:  All competent persons must receive a four-day training course from an EPA or DEP accredited program and pass an examination with a minimum score of 70%.

          - All asbestos Refresher Courses:  All workers and competent persons must attend a one-day EPA or DEP accredited refresher course annually.

          - Lead workers:  All workers must receive training pursuant to the requirements of 29 CFR 1926.62, 29 CFR 1926.59,and 29 CFR 1926.21.

        - Safety Compliance:  In addition to detailed requirements of this specification, comply with laws, ordinances, rules, and regulations of federal, state, regional, and local authorities regarding handling, storing, transporting and disposing of asbestos and or lead waste materials.  Comply with the applicable requirements of the current issue of 29 CFR 1910.1001; 40 CFR 61, Subparts A and B; and 29 CFR 1926.1101.  Submit matters of interpretation of standards to the appropriate administrative agency for resolution before starting the work.  Where the requirements of this specification and referenced documents vary, the most stringent requirement shall apply.

        - Respirator Program:  Establish a respirator program as required by 29 CFR 1910.1001 and 1926.1101.  This program will comply with all paragraphs of 29 CFR 1910.134.

      - PROJECT SECURITY

        - The Contractor is responsible for maintaining effective security of the project.

        - Entry into each work area shall be limited to the Engineer's Authorized Representatives, Owner's Authorized Representatives, and Government Agency's Representative authorized to inspect the project.

        - The Contractor shall provide entry for the Engineer and the Asbestos Air Monitor(s) to validate compliance with all abatement requirements.

        - Visiting personnel entering work areas must be provided with personal protective equipment as specified.

      - REMEDIAL CONTROLS

        - It is the responsibility of the Contractor to ascertain that the specifications are followed.  If the situation is not covered by the specifications, the Engineer shall be contacted to obtain remedial controls.

      - DELIVERY AND STORAGE

        - Deliver all materials in the original packages, containers or bundles bearing the name of the manufacturer and the brand name.

        - Store all materials subject to damage off the ground, away from wet or damp surfaces, and under cover sufficient enough to prevent damage or contamination.  Replacement materials shall be stored outside of the work area until abatement is completed.

        - Damaged, deteriorating or previously used materials shall not be used and shall be removed from the work site and disposed of properly.

        - Asbestos-contaminated waste and lead contaminated waste shall be stored in separate areas, containers or trucks from new materials and supplies.

      - SUBMITTALS

        - Submittals must be received in accordance with and indexed in the order of the Submittal Index that follows before any material or equipment is purchased or work performed.  The Contractor shall submit to the Architect/Engineer for review six (6) copies of the information required on the Submittal Index in this section.  The adequacy and accuracy of submittals and their compliance with contract documents are the responsibility of the Contractor.  All reviewing actions taken by the Architect/Engineer will in no way relieve the Contractor of his quality control requirements.

        - Work Practices and Procedures Asbestos:

          - Submit a written company Standard Operation Procedures of the work procedures to be used in the removal and demolition of materials containing asbestos to the Architect/Engineer

          - Submit a work schedule, weekly goals and objectives, minimum daily staffing, and removal methods summary.  The work schedule and weekly goals shall be illustrated on a bar graph.

          - The Contractor shall be responsible for the basic design of all work performed under this section, they shall submit a plan to include all phasing, the location of asbestos control areas, decontamination area, equipment decontamination enclosure, interface of trades involved in the construction, sequencing of asbestos-related work, sequencing of asbestos-related work, disposal plans, type of wetting agent and sealant to be used for asbestos removal, personal air monitoring program and a detailed description of the method to be employed to prevent fiber release,..  Show point of controlled access to the building for transporting asbestos-containing building material from the regulated area to the exterior of the building.  Show auxiliary make-up air points, location of HEPA exhaust ventilation unit location of HEPA exhaust and location of pressure differential meter sensor.  This plan must be approved by the Engineer prior to the beginning of any asbestos and or lead abatement work.

        - Engineering and Work Practice Controls for Lead abatement:

          - The contractor shall submit as part of the safety plan a written plan showing how the following work practices shall be implemented:

            - The Contractor shall implement work practice controls, including administrative controls, as required by OSHA 29 CFR 1926.62.

            - The Contractor shall implement work practice controls to prevent exposure to the staff and population of the facility where the lead removal occurs and where impact to concrete and or gypsum surfaces can cause a release of silica dust.

            - The contractor shall implement work practice controls, including administrative controls, as required by OSHA 29 CFR 1926.1000.

        - Additional Worker Protection During Exposure Assessment:  In addition to respiratory protection, the Contractor shall provide the following:

          - Protective Clothing shall be provided for workers and authorized visitors entering work area.  Reusable and/or disposable protective whole body clothing (Contractor's option) to include head coverings, gloves, and foot coverings.  Sleeves and foot coverings shall be made secure at the ankles and wrists by the use of tape.  Protective clothing shall be provided to all workers and authorized visitors in sizes adequate to accommodate movement without tearing.

          - Foot Protection:  Non-skid footwear shall be provided.

          - Eye Protection:  Provide goggles in accordance with ANSI Z87.1 to personnel engaged in lead-based paint removal when a full face respirator is not required.

          - Change Areas shall be equipped with separate storage facilities for protective work clothing and equipment and for street clothing and shall prevent cross contamination.

        - Decontamination Facilities (Showers) shall be provided and shall be located between the storage facility used to store protective work clothing and the change area used to change out of street clothing

          - The lead coating shall be removed sufficiently to allow for welding and/or torch cutting of structural members.

          - The contractor shall also have on site a Lead Compliance program as required under 29 CFR 1926.62 (e)(2)

        - Safety Plan:  The Safety Plan must be on site at all times and is to include, but not be limited to, the following:

            - Type, quantity and location of fire extinguishers.

            - Lock-out/Tag-out Program and any other pertinent electrical information.

            - Type of eye and ear protection.

            - Location of emergency breakthrough point if different from the drawings.

            - Type, quantity and location of first-aid kits.

            - Times and usage of hard hats.

            - Safety training afforded employees.

            - Roof safety system to be used.

            - Provisions for avoiding heat stress.

            - Employee exposure assessment for lead.

          - Decontamination and Work Procedures:  Submit project specific decontamination and work procedures that will be followed on this project.

          - Project Log:  A Project Log will be maintained throughout the project by the Contractor.  The log will contain notes concerning any accidents that may happen and any deviation from standard work procedures and any other pertinent project information.  At project completion, the original of this log will be submitted to the Architect/Engineer as part of the permanent job file.

          - Daily Containment Log In/Out Form:  The Daily Containment Log In/Out form will be kept on a clipboard in the clean room of each decontamination unit.  The Contractor will ascertain that everyone who enters and leaves the containment will sign in/out.  At project completion, the log will be copied and made part of the post submittal package.

        - Equipment and Material to be Utilized:

          - Material Safety Data Sheets:

            - Submit a notarized statement documenting the Material Safety Data Sheets and Hazardous Communication Standard Training is complete and guarantee that all products used on site are complete for Material Safety Data Sheets and hazard communication requirements and that each employee has been trained in the Hazard Communication Standard.

            - Material Safety Data Sheets for any product containing any kind of chemical the Contractor will be utilizing on the project will be on site at all times.

            - Submit copies of all MSD Sheets directly to the General contractor and the owner as required for compliance with their respective Hazard Communication Programs.

        - Notification Requirements:

          - Insurance and Contract Security:  Submit copies of all insurance policies or certificates of insurance and performance and payment bonds required under this contract.

          - Notifications:  For all asbestos work subject to Maine DEP Chapter 425 latest additions and in accordance with 40 CFR 61.145 and 40 CFR 61.146 (Demolition/Renovation Notification Information Sheet), notification must be submitted by the Contractor to the Maine Department of Environmental Protection, Bureau of Solid Waste, State House Station #17, Augusta, Maine 04333, with a copy to the Architect/Engineer for review 15 days prior to the commencement of the work.

          - Landfill Approval Evidence: Submit written evidence to the Architect/Engineer that the landfill for disposal is approved for asbestos and or lead disposal respectively by the Department of Environmental Protection of the state in which the landfill is located.

          - Dry Removal Request:  If dry removal is requested in the asbestos plan, submit copies of the approval received from the Maine Department of Environmental Protection.  Submittals are to be received by the Architect/Engineer prior to any removal being done.

        - Personnel, Training, Medical, and Respiratory Fit Test Documentation.

          - Respirator Protection Program:  A summary of the Contractor's Respiratory Protection Program as required by 29 CFR 1910.134 must be on site at all times.

          - Personnel Training Certificates, Medical Exams, Medical Questionnaires, and Respirator Fit Tests:

            - Training Requirements:  Submit to the Architect/Engineer certificates of training for each employee.  Note:  The exterior roof abatement is now not regulated by DEP Chapter 425 provided they are not sanded, grinded, abraded, or cut with a mechanical roof cutter.  Thus if work is to be done in a manner so as to not come under these rules OSHA training is required.  For all other work under this section provide the following:

              - Workers:  All workers must receive a training course from an EPA accredited program and pass an examination with a minimum score of 70%.

              - Competent Person:  All competent persons must receive a Supervisor training course from an EPA accredited program and pass an examination with a minimum score of 70%.

              - Refresher Course:  All workers and competent persons must attend an EPA accredited refresher course annually.

              - Submit proof of Maine DEP certification for all employees on the project.  This does not relieve employees of their responsibility to have their certificate on site.

              - Submit proof of Maine DEP Asbestos Contractor's License.

              - Lead workers:  All workers must receive training pursuant to the requirements of 29 CFR 1926.62, 29 CFR 1926.59,and 29 CFR 1926.21

            - Medical Exams:  Proof of medical exams as required by 29 CFR 1910.1001 and 29 CFR 1926,62 must be on site at all times.

            - Medical Questionnaires:   A notarized statement that medical questionnaires have been administered in accordance with 29 CFR 1910.1001 and 29 CFR 1926.1101 - must be on site at all times.

            - Respirator Fit Tests:   Proof of respirator fit testing for all employees to be employed on the project.  Fit testing will be in accordance with 29 CFR 1910.1001 - and 1926.1101 and must be on site at all times.

          - New Employee:  All of the information in E.2 of this section must be on site prior to any employee being allowed to perform any abatement activities.

      - SHOP DRAWINGS

        - Shop drawings prepared by the Contractor or his Subcontractors or suppliers for submission shall be signed and approved by the Contractor before submission.  In particular, the Contractor shall ascertain that the drawings meet all requirements of the contract documents and conform to the conditions at the job site.  Furthermore, the Contractor shall be fully responsible for observing the need for and making any changes.  If the shop drawings show variations from contract drawings or specifications, whether because of standard shop practice or other reasons, the Contractor will not be relieved of the responsibility for completing the work in full accordance with the contract documents even though such shop drawings are reviewed by the Architect/Engineer.

        - Contractor to determine and verify field construction criteria and conformance of submittal with requirements of contract documents.

        - Contractor to sign or initial each sheet of shop drawings to certify compliance with requirements of contract documents.  Notify Architect/Engineer, in writing, at time of submittal of any deviations from requirements of the contract documents.  The review of the submittals by the Architect/Engineer shall not be construed as a complete check but will only indicate the general method of construction and detailing is satisfactory.  Review of such submittals will not relieve the Contractor of the responsibility for any error which may exist as the Contractor shall be responsible for the dimensions and design of adequate connections, details, and satisfactory construction of all work.

        - Do not fabricate products or begin work which requires submittals until submittals are returned by the Architect/Engineer.  All work shall be in conformance with reviewed shop drawings.

        - Shop drawings shall be drawn to scale and show all necessary dimensions and details.  They shall be numbered consecutively, dated, and indicate the project name, the names of the Contractor and Subcontractor, the name and description of the equipment or articles shown, the manufacturer's name, the kinds, types, grades, thickness and finishes of materials, including all fittings.  Marked-up copies of standard drawings showing typical conditions and details and indicating their specific application to the work will not be acceptable.  Shop drawings shall be accompanied by a letter of transmittal identifying the items of work submitted.  Shop drawings shall be submitted in accordance with the Submittal Index.  The review of the shop drawings will be general and shall not relieve the Contractor from sole responsibility for errors or omissions of any sort.  Review will not imply verification of required quantity of material, nor correctness of dimensions.  Requests by the Architect/Engineer for changes and corrections on shop drawings shall not be construed as an order for extra work under the contract.

      - SUBMITTAL REQUIREMENT

        - Apply Contractor's stamp, signed or initialed certifying to review, verification of products, field dimensions and field construction criteria, and coordination of information with requirements of work and contract documents.

        - Coordinate submittals into logical groupings to facilitate interrelation of the several items.

      - SUBMITTAL INDEX

        - All of the following must be submitted in sextuplet (six sets) to the Architect/Engineer, if applicable, not less than fifteen (15) calendar days prior to the start of abatement.

          - Written abatement plan as specified in paragraph 1.7 (B) of this section.

          - Work Practices and Procedures:

            - Standard Operating Procedures

            - Historical data from previous projects if the Contractor is not planning on using a test containment (roofing and siding and lead removal  projects only)

            - Decontamination and Work Procedures

          - Notification Requirements:

            - DEP Notification

            - Landfill Approval Evidence

          - Personal Training and Certification for asbestos workers: For all employees including the Asbestos designer, and independent asbestos air monitor performing asbestos activities that are regulated by Maine Chapter 425.

            - Training Certificates

            - Evidence of Maine DEP Employee Certificate

            - Evidence of Maine DEP company license.

          - Personal Training and Certification for lead workers and asbestos workers that remove asbestos that is not regulated by Chapter 425:

            - Proof of Required OSHA training for the work being performed.

      - SUBMITTAL INDEX AT COMPLETION OF PROJECT

        - The following must be submitted, to the Architect/Engineer if applicable, within ten (10) workdays of the completion of the abatement project in sextuplet (4 sets) these submittals will be reviewed for completeness and retained for the owners use no copies will be returned to the contractor.

          - Work Practices and Procedures:

            - Project Log

            - Daily Containment Logs.

            - Evidence of Negative Air (Strip Charts).

            - Results of Personal Air Monitoring, including Air Sampling Pump Calibration Records.

            - Disposal Receipts, Asbestos and Lead.

            - Air Monitor's signed statement of visual inspection for each clearance.

            - TCLP test reports.

      - ADDITIONAL SUBMITTALS

        - The following must be submitted, to the Architect/Engineer if applicable, within ten (10) workdays of receiving the letter of intent.

          - Cost breakdown and requisition for payment.

          - Any additional submittals shown under their respective sections.

      - AIR SAMPLING

        - The Contractor shall provide all on site monitoring, sampling and laboratory services for area air monitoring, and all, visual inspections and independent air clearance sampling and analysis.

        - Air sampling shall be conducted in accordance with the AHERA Interim TEM Nonmandatory Analytical Method and the NIOSH Standard Analytical Method 7400 for the sampling and analysis of airborne asbestos fibers.

        - Personal Samples:  Sampling and analysis shall be in accordance with NIOSH Method 7082 for lead

        - Background samples may be collected prior to initiation of abatement activity in each area.  A sufficient number of samples must be taken which are statistically unbiased and representative of airborne fiber concentrations throughout the asbestos-affected area.  For multiple room containments, background samples must be collected in each room.

        - Area and Personal Sampling:

          - Air Sampling Pumps: Two types of pumps shall be used to sample airborne asbestos fibers.

            - Personal samples shall be collected with a low flow pump which is capable of sampling at flow rates ranging from 0.5 liters/minute to 2.5 liters/minute.  The pump is hung from the worker's belt and attached to a filter cassette positioned in the worker's breathing zone (within 9 inches of the mouth) by means of plastic tubing and lapel clip.

            - Area samples shall be collected with a stationary high volume pump which is capable of sampling at flow rates ranging from 0.5 liters/minute to 16 liters/minute.

            - Air sampling pumps must be calibrated before and after each use by means of a primary standard or by a secondary standard (e.g., rotameter) that has been calibrated against a primary standard within the last 30 days.

            - Pumps must have a tag attached including the last calibration date and the initials of the technician performing the calibration.

          - Filters:  Three types of filters can be used.

            - Phase Contrast Microscopy:  Cellulose ester with 0.8 to 1.2 micron pore size.

            - Transmission Electron Microscopy:  Polycarbonate with 0.4 micron pore size or cellulose ester with 0.8 micron pore size.

          - Cassettes and Blanks:  A 3-piece, 25 mm open-faced cassette which contains a membrane filter, a support pad and two sealing caps is used for air sampling.  A minimum of two blanks must always be submitted for analysis or 10 percent of total samples, whichever is greater.

          - Number of In-Progress Samples:  Dependent on the size of the regulated area, the number of in-progress samples required varies.  The number of samples specified below are intended as guidelines; however, the actual numbers may be increased or decreased based upon site constraints and the professional judgement of the Asbestos Air Monitor:

            - For Containments of 500 s.f. or Less:

              - A minimum of two samples inside.

              - Two samples outside of containment but within the extended regulated area located upwind and downwind of the containment.

              - One sample at a HEPA exhaust outlet.

              - One sample in the decon clean room.

            - For Containments Greater than 500 s.f.:

              - A minimum of three samples inside.

              - Two samples outside of containment but within the extended regulated area located upwind and downwind of the containment.

              - One sample at a HEPA exhaust outlet.

              - One sample in the decon clean room.

            - For outside removal by licensed Abatement Contractors performing roofing and siding abatement:

              - No area monitoring is required provided the personal air monitoring results do not exceed the OSHA PEL Standard of 0.1 f/cc as based upon an 8-hour TWA.

          - Number of Clearance and Final Clearance Samples for Roof Containments (Test Containments):  Dependent of the size of the regulated area, the number of clearance samples varies.  Passive sampling procedures for clearance will be used for all roof containments.  The number of samples specified below are intended as required guidelines; however, the actual number may be increased or decreased based upon site constraints and the professional judgement of the Asbestos Air Monitor:

            - In-progress samples, as described in 4.a.1 and 4.b.1, may be utilized for clearance samples if the fiber concentration is 0.10 f/cc or less.

            - If the fiber concentration is above 0.10 f/cc, conduct additional sampling, as described in 4.a.1 and 4.b.1, to achieve a fiber concentration of 0.10 f/cc or less.

            - In cases where fiber concentrations at background level are above 0.10 f/cc, the acceptable clearance fiber concentration will be at background or less.

            - Fiber Density and Sample Volume:  The NIOSH 7400 Method has a validation range of 100 f/mm-sq to 1300 f/mm-sq of filter area (or 78.5 fibers/100 fields to 1014 fibers/100 fields).  The State has chosen 78.5 fibers counted in 100 fields (100 fibers/mm-sq) as the recommended acceptable fiber density or loading for air samples.  In the absence of this loading on the filter, a sufficient air volume must be collected to verify that the recommended fiber density requirement could not be met.  The calculation for required sample volume (RSV) at 0.10 fibers/cc) is as follows:

- RSV (in liters) = [(78.5 fibers/100 fields)x(385 mm-sq/filter)]

- [(0.10 fibers/cc)x(1000 cc/1)x(0.00785 mm-sq)]

- = 3850 liters

            - For outside removal by licensed Abatement Contractors performing roofing or siding abatement, clearance sampling is not required; however, a visual inspection by an independent Asbestos Air Monitor is required as per Maine DEP Asbestos Management Regulations Chapter 425, Section 9(A)(16)(b)(ii).

          - Personal Sampling:

            - Personal samples shall be collected and analyzed in accordance with the OSHA reference method (ORM).  See U.S. Department of Labor: Occupational Safety and Health Administration; Occupational Exposure to Asbestos; Title 29 CFR 1910.1001, "General Industry Standard," and Title 29 CFR 1926.1101, "Construction Standard," by the Asbestos Abatement Contractor.

              - Personal samples, representative of worker's exposure, must be taken during each shift.  As a minimum, 25 percent of the work crew must be sampled.  Documentation for personal sampling must be available at the job site for review.  Collection of personal samples is the responsibility of the Asbestos Abatement Contractor.

            - Records shall be maintained at the job site which include all personal air sampling data.  Documentation for personal samples must contain the following information and be recorded as part of the documentation for each sample collected:

              - Sample number

              - Name and Social Security Number

              - On and off time of sample

              - Sample duration

              - Pre- and post-flow rate

              - Total volume

              - Fiber count

              - Fiber density

              - Fiber concentration

              - Limit of quantization

              - Limit of detection

              - Laboratory coefficient of variation (CV)

              - Job name and number set by the Division

              - Date collected and date analyzed

              - Sample collector's and analyst's signature

              - Name of Analytical Laboratory

            - Personnel performing "personal sampling" must successfully complete a course in air sampling procedures.

            - Flow rates must be checked before and after each sampling period.  Rotameters used for this purpose must be calibrated monthly against a primary standard.

        - An asbestos abatement work area may not be reoccupied until

          - Clearance air monitoring samples are collected by an independent Asbestos Air Monitor using the air sampling methods prescribed by this section at a minimum.

            - Air Clearance Sampling - Phase Contrast Microscopy:

              - An independent Asbestos Air Monitor determines that the average total fiber count of the samples collected in the work area is equal to or less than 0.010 f/cc (fibers per cubic centimeter) of air as analyzed by phase contrast microscopy.

              - The minimum number of air clearance samples were collected as follows:

                - Two samples for activities that contain less than 100 combined linear and square feet of friable ACM.

                - Three samples for activities that contain more than 100 but less than 1,000 linear and or square feet of ACM.

                - Five samples for activities greater than 1,000 linear and or square feet of ACM.

              - Air clearance samples must contain at least 2452 liters of air, and sampling flow rates must not exceed 16 liters of air per minute.

              - Air samples must be collected utilizing aggressive techniques, that are consistent with 40 CFR, Part 763, Subpart E ( effective date December 14, 1987).

              - In the event that the inside area clearance samples fail (> 0`.010 f/cc), the Contractor shall:

                - Reclean the area at no cost to the Owner. or

                - Resample by Transmission Electron Microscopy to obtain a clearance as per the Asbestos- Containing Materials in Schools rule 40 CFR Part 763 ( effective October 30,1987); or

                - Exclude potentially contaminated make up air and resample.

            - Aggressive Air Clearance Sampling:

              - Blow Down:  Direct the exhaust from appropriately sized leaf blower against all containment walls, ceilings, and other surfaces to render any remaining fibers airborne.  Five minutes per 1,000 sq. ft. of floor area is required.  Decontaminate (or discard) the leaf blower after each use.

              - Air Movement:  Place a 20-inch propeller fan in the center of the containment and ensure it remains activated during the sampling period.  One fan should be used for each 10,000 cubic feet.

            - Air Sampling:  Collect the requisite number of air samples the required time to ensure adequate sample volumes.

            - Completion of Sampling:  Turn off the pump and then the fan when sampling is complete, and submit the cassette for analysis.

            - Sampling Restriction:  Aggressive air sampling shall be performed at all times for clearance of the regulated area.

- PRODUCTS

      - MATERIALS

        - Polyethylene Sheeting for walls and stationary objects shall be a minimum of 4-mil thick.  For floors and all other uses, sheeting of at least 6-mil thick shall be used in widths selected to minimize the frequency of joints.

        - Polyethylene Sheeting utilized for the worker decontamination enclosure shall be opaque white or black in color.

        - Reinforced Polyethylene Sheeting:  Where the exterior plastic sheet is the only separation between the work area and the immediate occupied building area, provide translucent, nylon reinforced, laminated, polyethylene film.  Provide largest size possible to minimize seams, 4- or 6-mil thick, frosted or black.

        - Acetate, clear size 36" x 36".

        - Disposal Bags shall be of 6-mil polyethylene, pre-printed with labels as required by OSHA.  Label specifications shall comply with 29 CFR 1910.1001 and 1926.1101.

        - Disposal Drums shall be metal or fiberboard with locking ring tops.

        - Warning Signs and Labels:  Provide warning signs at all approaches to asbestos control areas containing concentrations of airborne asbestos fibers.  Locate signs at such a distance that personnel may read the sign and take the necessary protective steps required before entering the area.  Provide labels and affix to all asbestos materials, scrap, waste, debris, and other products contaminated with asbestos.  Labels and signs will comply with 29 CFR 1910.1001 and 1926.1101.

          - Warning Sign:  Vertical format conforming to 29 CFR 1910.145 and 1926.1101 shall be a minimum size of 20" by 14" displaying the following legend in the lower panel:

DANGER								1" Sans Serif, Gothic or Block

ASBESTOS							1" Sans Serif, Gothic or Block

CANCER AND LUNG DISEASE HAZARD		3/4" Sans Serif, Gothic or Block

AUTHORIZED PERSONNEL ONLY			1/4" Gothic

RESPIRATORS AND PROTECTIVE

CLOTHING ARE REQUIRED IN

THIS AREA							1/4" Gothic

Spacing between lines shall be at least equal to the height of the upper of any two lines.

          - Labels:  Provide labels of sufficient size to be clearly legible, displaying the following legend:

DANGER

CONTAINS ASBESTOS FIBERS

AVOID CREATING DUST

CANCER AND LUNG DISEASE HAZARD

          - DO NOT ENTER signs - minimum size 6" x 12" with 2" letters - red on white shall be furnished.

          - Barrier Tape:  Red or Yellow with warning - "DANGER - ASBESTOS - DO NOT ENTER."

        - Surfactant:  (Wetting agent) shall be a 50/50 mixture of polyoxyethylene ether and polyoxyethylene ester, or equivalent, mixed in a proportion of 1 fluid ounce to 5 gallons of water or as specified by the manufacturer.  (An equivalent surfactant shall be understood to mean a material with a surface tension of 29 dynes/cm as tested in its properly mixed concentration, using ASTM method D1331-56 "Surface and Interfacial Tension of Solutions of Surface Active Agents.")  Where the work area temperature may cause freezing of the amended water solution, the addition of ethylene glycol in amounts sufficient to prevent freezing is permitted.

        - Towels will be disposable type and minimum size of 24" x 36" per towel.

        - Spray Adhesive shall not be noxious or toxic to workers or subsequent users of the area.  Spray adhesive must not contain methylene chloride.

        - Make-up Air Filters:  Filter to be 24" x 24" equal to Farr 30/30 Class II, mounted in a Type 8 Universal Holding Frame (#79473-004).

        - Duct Tape:  Provide duct tape in 2" or 3" widths with an adhesive which is formulated to aggressively stick to polyethylene sheet.

        - Lumber:  Provide kiln dried 1" x 3" strapping, 2" x 3" and/or 2" x 4" framing lumber of any grade or species.

        - Foam Sealant:  Provide fire stop foam sealant in aerosol cans which is specifically formulated to expand, solidify, and seal penetrations and openings.

        - Extension Cords:  Extension cords utilized in the containment will be a minimum 12/2 wire with ground, neoprene or rubber covered.  Extension cords will be utilized in accordance with the National Electrical Code.

        - Physical Barrier:  3/8" plywood, emergency exit door, surface mounted bolt-lock, acetate window, hasp, staple and padlock.

      - GENERAL EQUIPMENT

        - Portable Exhaust Ventilation Unit Equipped with HEPA Filters shall be in accordance with ANSI Z9.2.  Equip with absolute (HEPA) filters.  There must be sufficient equipment to maintain a minimum pressure differential of minus 0.02 inch of water column relative to adjacent, non-abatement areas.  Filters on vacuums and exhaust equipment shall conform to ANSI Z9.2.

The Portable Exhaust Ventilation Unit equipped with HEPA filters shall have the following:

          - Magnehelic gauge to monitor the unit's air pressure difference across the filters.

          - Audible alarm with or without flashing red light for unit shutdown.

          - A yellow warning light to indicate a decrease in air flow due to filter loading.

        - Negative Pressure Recorder with paper printout to record negative pressure.  Instrument to have an audible alarm.  Printout range must be from .00 to .05.

        - Respirators:  Select respirators from those approved by the National Institute for Occupational Safety and Health (NIOSH), Department of Health and Human Services.

          - Powered Air Purifying Respirator (PAPR) with high-efficiency filter and full facepiece with rechargeable batteries.

          - Type C Respirators with an air supply system that will provide Grade D breathing air in accordance with OSHA 29 CFR 1910.134 and ANSI 286.1-1973 Commodity Specification for Air.  The compressed air systems shall have a receiver of adequate capacity to allow escape of all respirator wearers from contaminated areas in the event of compressor failure.  Compressors must meet the requirements of 29 CFR 1910.134(d).  Compressor to have alarms that indicate a high temperature and carbon monoxide.

          - Asbestos-rated respirator, North 7700 or equivalent, using NIOSH rated filters for asbestos North 7500-8 or approved equal.

        - Protective Clothing:  Provide workers and authorized visitors exposed to airborne concentrations of asbestos fibers with disposable protective whole body clothing to include underwear, head coverings, gloves, and foot coverings.  Sleeves and foot coverings shall be made secure at the ankles and wrists by the use of tape.  Protective clothing shall be provided to all workers and authorized visitors in sizes adequate to accommodate movement without tearing.

        - Working Clothing:  Non-skid footwear shall be provided to all abatement workers.

        - Eye Protection:  Provide goggles in accordance with ANSI Z87.1 to personnel engaged in certain asbestos operations when a full face respirator is not required.

        - Electrical:  Provide ground-fault circuit interrupters for all electrical equipment.

      - REMOVAL EQUIPMENT

        - A sufficient supply of scaffolds, ladders, lifts and hand tools (e.g.,  scrapers, wire cutters, brushes, utility knives, wire saws, etc.) shall be provided as needed.

        - Sprayers with pumps capable of providing 500 pounds per square inch (psi) at the nozzle tip at a flow rate of 2 gallons per minute for spraying amended water.

        - Rubber dustpans and rubber squeegees shall be provided for cleanup.

        - Brushes utilized for removing loose asbestos-containing building material shall have nylon or fiber bristles, not metal.

        - A sufficient supply of HEPA-filtered vacuum systems shall be available during cleanup.

      - GLOVE BAG

        - Glove Bag:  Zipper type - Safe-T-Strip, Profo Type or approved equal.

        - HEPA Vacuum:  High-efficiency particulate HAKO Model C80315 or approved equal.

        - HEPA Exhaust Unit:  Exhaust unit equipped with absolute (HEPA) filters, exhausted to outside the building to provide six (6) air changes an hour.

        - Respirator:  Dual cartridge asbestos-rated respirator, Norton 7700 or equivalent, using NIOSH rated filters for asbestos, Norton 7500-8 or approved equal.

        - Disposable Clothing:  Tyvek disposable coveralls or equivalent; hoods and booties (separate or as part of coverall).

        - Asbestos Disposal Bags:  6-mil thickness minimum with asbestos warning printed or pasted on bag.

        - Water Pump Sprayer:  One to five-gallon capacity.

        - Surfactant:  A wetting agent to add to water to increase penetrating ability.  Water with surfactant added is called "amended water."  Aqua-Gro or equivalent.

        - Duct Tape:  Preferably 3" width.

        - Double Sided Tape:  Preferably 2" to 1" width, #4962 as manufactured by the 3M Company or approved equal.  Tape to be adhesive-backed.

        - Wettable Cloth:  A glue-impregnated cloth used in sealing exposed insulation left in place.  H.R. Allen R-2550 or equivalent.

        - Pipe Insulation End Caps:  Alternative to wettable cloth.

        - Spray Glue:  Used to seal exposed remaining asbestos insulation if wettable cloth or end caps are unavailable.  Asplundh Spray Adhesive or equivalent.

        - Barrier Tape:  Red or Yellow with warning - "DANGER - ASBESTOS - DO NOT ENTER."

        - Warning Signs:  White with black and red lettering stating asbestos dust may be present and to wear appropriate protection.

        - Bone Saw (Flexi-Saw):  Disposable or reusable.  For cutting any thickness of insulation, but primarily where razor knife or hook knife is too short.

        - Razor Knife:  Disposable or reusable.

        - Hook Knife:  Disposable or reusable.

        - Damp Rag:  Used to wipe metal pipe clean of asbestos particles.

        - Wire Snips:  Used to cut wire or metal bands used to hold insulation to pipe.

        - Metal or Fiber Drum:  35- to 55-gallon capacity drum with sealable top, marked to indicate asbestos contents.

        - Designated Shower Area:  Either portable or existing in building in case of accidental contamination.

      - ENCAPSULANTS

        - Encapsulation materials shall be as follows:

- Wettable Cloth:  Fiber lock Lag Cloth or approved equal.

- Spray Type Encapsulant:  Combination of Penetrating - Bridging - Fiberlock Asbestos Binding Compound Concentrate or approved equal.

- Bridging Encapsulant:  Mastic formulation to provide a tough, non-porous membrane over acoustical plasters, cementitious fireproofings, and all thermal insulations.  Maintain flexibility.  Penetrate up to 3/16".  American Coatings-Cable Coating 2B or approved equal.

- Penetrating Encapsulant:  One component.  Imparts an elastic-like resiliency to treated substrates with a durable and impact resistant surface.  American Coatings Cable Coating 22P or approved equal.

- Soil Encapsulant:  Penetrates into the top layer of asbestos-contaminated soil, binds asbestos fibers in place, and generates a hard, rigidly sealed surface.  American Coatings-Cable Coating Earth-Kote Process or approved equal.

- High Temperature Sealant:  High temperature thermal sealant to permanently seal any remaining fibers in place.  American Coatings FNE or approved equal.

- EXECUTION

      - WORK SEQUENCE AND SPECIAL INSTRUCTIONS FOR INTERIOR ABATEMENT

        - INTENTION

          - Nothing in this section shall supercede the phasing or coordination sections of this manual or phasing and scheduling by the General Contractor.

          - This project includes the design and removal of the asbestos containing building materials, as follows:

            - Provide a written design and drawings for the abatement of this facility.  This design shall be submitted for review of the engineer 15 days prior to the start of the abatement.

            - All Pipe insulation (TSI) on all piping, including all fittings, that is exposed now or during the demolition and renovations of the facility shall be abated.

            - Patch compound on the maintenance bay roof tested positive for asbestos, so all troweled on patch compound including patch compound under the existing EPDM roof shall be assumed as asbestos containing.  All roof patches must be removed in accordance with the latest OSHA and DEP regulations.

          - This project includes the, removal and or preparations of lead coated surfaces to allow for the removal of existing Girders/trusses as identified on the Demolition plans.  The contractor shall be responsible to coordinate with other trades for the layout of areas requiring lead abatement.

          - The following surfaces have been identified by a lead survey conducted by a state licensed inspector to contain lead coated surfaces.

            - All steel columns and steel girder members tested greater than 0.02 mg/Ft2 by XRF.  (Any XRF reading above 0.02 mg/Ft2 should be considered as containing lead based substances.)  These members will require removal of lead coatings to facilitate the cutting and removal of some members.

            - Under section 05120 Structural Steel and section 05500 Metal fabrications it is specified to remove or disconnect all bolted connections by unbolting and to restrict the lead abatement to areas that require cutting and or modifications (welding) to lead coated  steel members.

        - SPECIAL INSTRUCTIONS

          - Submittals:

            - Submit cost breakdown for Requisition for Payment as required by the General Contractor.

            - Submit Asbestos design by a licensed Asbestos Designer.  Include designers License and training certificates.

          - Applicable Regulations:

            - Federal OSHA Regulations apply to this project.  AHERA regulations apply to this project.

            - State DEP Regulations apply to this project.

          - Electrical:

            - All circuits individually GFI-Protected.

            - Weatherproof enclosure NEMA 3 (raintight) and receptacle covers.

            - Durable 16 gauge steel construction.

            - Each interior and exterior power supply board shall have one (1) 20-amp circuit for the Asbestos Air Monitor to perform air monitoring and clearance air monitoring without power interruptions.

            - Power Source:  Temporary power shall provided as be specified under Division 1.

          - Site Specific Work Practices:

            - No abated surface shall receive lockdown, or encapsulant prior to air clearances.

            - DEP notification is required by the Contractor.  The contractor may request waivers as required to reduce poly containment as allowed in the DEP chapter 425 regulations.

            - The Contractor shall use P.P.E. during all abatement.

            - The Contractor shall be responsible for personal air monitoring during all abatement.

            - The Contractor shall be responsible to provide and pay for a visual inspection and Air Clearance by an independent Asbestos Air Monitor as required by Maine DEP Asbestos Management Regulations.  A signed statement shall be completed by the Asbestos Air Monitor for each visual inspection and Air Clearance with the following information:

              - 1.	Description of area of visual inspection/clearance.

              - 2.	Name, date, and Maine DEP certificate number of Air Monitor.

              - 3	Signed statement that visual inspection/Air Clearance was performed and the results, with an indication of the meaning of the results(passed or  failed).

          - Make-Up Air Filters shall be securely framed and have a poly flap that extends a minimum of four inches outside filter.  Filters will be installed only on true vertical surfaces or a surface that leans outward at the top from inside the containment.  This procedure will allow the flap to have a positive seal upon loss of negative pressure.

            - Temporary Lighting:

              - Provide a well lit workplace during both removal and inspections.

              - Comply with OSHA regulations 1926.405(a)(2) Wiring Methods - Temporary Wiring and 1926.405(g) Flexible Cords and Cables.

              - Acceptance of Work Area Prior to Air Clearance:  Clean will be determined by ASTM E1368-90.

              - Equipment and Staging:  The Contractor shall be responsible for any and all tools, equipment and staging which is required for access to the removal area.

        - ASBESTOS WORK SEQUENCE AND PERFORMANCE

          - Work Sequence minimum requirements:

            - Install asbestos control barrier rope and "keep out" signs as required.  Maintain this barrier throughout each phase.

            - Install physical barriers where required.

            - Install critical barriers at all windows, doors, and wall penetrations and over HVAC duct and equipment.  When working in areas with telephone equipment and/or motors to remain in place, maintain ventilation via filters, ducts or chases as required.

            - Install negative air machines.  Install temporary plywood panels at window  openings as required for security of containment.

            - Install containment as require to reduce work area to areas with asbestos containing materials.

            - Install and maintain negative pressure recorder.

            - Construct personal decontamination/waste transfer.

            - Establish negative air differential of 0.02" of water.  Add additional HEPA units if required.

            - Removal of asbestos-containing building materials:

              - Begin a systematic removal of asbestos-containing building materials using proper abatement methods.

              - Fine clean all surfaces asbestos-containing building materials were removed from.

              - Wet wipe all containment surfaces with a soap and water solution.

              - Visual inspection by an independent Asbestos Air Monitor.

              - If visual inspection by independent Asbestos Air Monitor passes, the air monitor may start clearance air monitoring, following part 1.13 of this section.

              - If air clearance samples pass, then tear down and turn area over to the other trades.

              - If the visual inspection or the air clearance samples fail, reclean and retest until clearance criteria is met.

        - LEAD WORK SEQUENCE AND PERFORMANCE

          - Work Sequence minimum requirements:

            - Install control barrier rope and "keep out" signs as required.  Maintain this barrier throughout each phase.

            - Install physical barriers where required.

            - Install critical barriers at all windows, doors, and wall penetrations and over HVAC duct and equipment

            - Install negative air machines.  Install temporary plywood panels at window  openings as required for security of containment.

            - Install containment as require to reduce work area to areas with lead coatings to be abated.

            - Install and maintain negative pressure recorder.

            - Construct personal decontamination/waste transfer.

            - Establish negative air differential of 0.02" of water.  Add additional HEPA units if required.

            - Removal lead coatings:

              - Begin a systematic removal of lead Coating using mechanical methods.

              - Fine clean all surfaces lead Coating were removed from.

              - Wet wipe all containment surfaces with a TSP solution.

              - Visual inspection by an independent Lead inspector.

      - WORK PRACTICES

        - General Provisions:  Asbestos abatement shall comply with work practice requirements set forth in the Department of Environmental Protection Rules and Regulations and these specifications.

          - All asbestos abatement activity shall be performed only by those persons who have been duly licensed or certified to perform such work in accordance with the requirements of the Maine Department of Environmental Protection Regulations.

          - The Asbestos Abatement Contractor shall maintain the required information for each asbestos abatement project required by the Department of Environmental Protection Laws, Rules and Regulations, Paragraph 9A4.

          - All Lead abatement activity shall be performed only by those persons who have been duly licensed or certified to perform such work in accordance with the requirements of the Maine Department of Environmental Protection Regulations and or OSHA regulations 29 CFR Part 1926.62

      - WORKER PROTECTIONS

        - General:

          - All asbestos and lead abatement work will be performed in accordance with 29 CFR 1910.1001, 29 CFR 1926.1101, and/ or 29 CFR 1926.62 and as specified herein.  Personnel shall wear and utilize protective clothing and equipment as specified herein.  Eating, smoking, or drinking shall not be permitted in the asbestos or lead control area.  Personnel of other trades not engaged in the abatement of asbestos or lead shall not be allowed in the work area unless all the personnel protection provisions of this specification are complied with by the trade personnel.

          - Engineering controls will be used to minimize the airborne fiber concentration within the work area.  HEPA-filtered exhaust units will be used to maintain a minimum negative pressure of .02 inches of water within the work area.  A combination of personal protective equipment and work practices will also be used to further reduce employee exposure to asbestos fibers and or lead dust.

          - Provide all authorized visitors with protective clothing, headgear, eye protection, footwear, and hard hats as in the procedures described herein and afford them the use of all facilities to hold them free of contamination of asbestos fibers and or lead dust.

          - Provide and post in the clean room, the decontamination and work procedures to be followed by workers, as well as the results of the personal air monitoring.

        - Personnel Protection:

            - The employer shall select and provide at no cost to the employee respirators which will provide adequate protection to the employee as specified by Section 1910.1001(g) Table D-1 and Section 1926.1101(h) Table D-4. and 29 CFR 1926.62

            - Respiratory protection shall be worn by all persons potentially exposed to asbestos from the initiation of the asbestos abatement project until all areas have been given clearance.  Clearance shall be obtained by visual inspection and air monitoring conducted by the Asbestos Air Monitor.

            - Respirators for Handling Asbestos:  Until it is established that the average airborne concentrations of asbestos the employees will confront will not exceed 100 times the permissible exposure limits, powered air purifying respirators or Type C (continuous flow or pressure demand) supplied air respirators will be used.

              - Once the exposure limits have been established, the respirators presented in 29 CFR 1910.1001 that afford adequate protection at such upper concentrations of airborne asbestos fibers may be used.

              - The filters provided for both the cartridge respirators and the PAPR's shall be HEPA filters.  The Contractor shall provide each worker with a new set of filters at the beginning or each shift during each day of asbestos removal including final cleaning.  For each PAPR, the Contractor shall have two (2) fully charged batteries at the beginning of each shift; one battery shall be used for the first half of the shift, the other for the second half of the shift.

        - Protective Clothing:

          - Provide to all workers, foremen, and superintendents protective disposable clothing consisting of underwear, full body coveralls, head covers, gloves and 18" high boot type covers and reusable footwear.

          - Provide eye protection and hard hats as required by job conditions and safety regulations.

          - Reusable footwear, hard hats and eye protection devices shall be left in the "contaminated equipment room" until the end of the asbestos abatement work.

          - Upon completion of abatement, dispose of footwear as contaminated waste or clean thoroughly inside and out using soap and water before removing from work area or from equipment and access area.

          - All disposable protective clothing shall be discarded and disposed of as contaminated waste every time the wearer exits from the work space to the outside through the decontamination facilities.

          - The color of the disposable clothing worn outside the work area shall be a different color than the disposable clothing worn inside the work area.

          - The last name of the worker will be printed in plain large letters or a large number with a cross reference sheet in the clean room on the back of the protective clothing with a magic marker type pen.

        - Decontamination Procedures:

          - Each worker and authorized visitor without exception shall upon entering the job site remove all under and outer street clothes in the clean change room and put on a NIOSH approved respirator with new filters and clean, disposable protective clothing before entering the equipment room or the work area.

          - Each time he/she leaves the work area, each worker and authorized visitor shall:

            - Vacuum gross contamination from clothing before leaving the work area.

            - Proceed to the equipment room and remove all clothing except respirator.

            - Still wearing the respirator, proceed naked to the showers.

            - Clean the outside of the respirator with soap and water while showering.

            - Remove filters and wet them and dispose of filters in the container provided for the purpose.

            - Wash and rinse the inside of the respirator.  After showering, dry off with disposable towels.

          - Following showering and drying off, each worker and authorized visitor shall proceed directly to the clean change room and dress in street clothes at the end of each day's work or before eating, smoking, or drinking.  Before re-entering the work area from the clean change room, each worker and authorized visitor shall put on a clean respirator with new filters and shall dress in clean, disposable protective clothing except that worker intending to re-wear protective clothing stored in the equipment room shall enter the equipment room wearing only respirators.

          - Contaminated reusable work footwear shall be stored in the equipment room when not in use in the work area.  Upon completion of asbestos abatement, dispose of footwear as contaminated waste or clean thoroughly inside and out using soap and water before removing from work area or from equipment and access areas.  Store contaminated protective clothing in the equipment room for reuse or place in receptacles for disposal with other asbestos-contaminated materials.

          - Workers removing waste containers from the equipment contamination enclosure shall enter the holding area from outside wearing a respirator and dressed in clean disposable coveralls.  No worker shall use this system as a means to leave or enter the washroom or the work area.

      - FIRE PROTECTION

        - Automatic sprinkler control valves shall remain locked-open during the entire asbestos abatement project.

        - In the event that the valves must be closed, prior written approval from the Facility Representative shall be attained.  When sprinkler control valves are shut during the work shift, they should be reopened at the end of the shift so that the fire protection system is activated during all non-working times.  Documentation of the opening and closing of all valves shall be provided in the Project Log.

        - Fire extinguishers shall be provided inside the enclosed work area.  Type and quantity to be defined in the Safety Plan.

        - Fire extinguishers shall be provided outside the enclosed work area in storage areas.

        - An air horn shall be provided and hung by each fire extinguisher.

        - Prior to project start-up, (1) the workers shall be trained on the safe use and handling of fire extinguishers, (2) informed of the locations of all fire protection equipment, (3) the location(s) of the sprinkler control valves, and (4) documentation of the above shall be recorded in the Project Log.

        - Prior to the performance of any cutting or welding, the supervisor shall be notified, a fire watch shall be stationed  and provided with a fire extinguisher, and appropriate respirators shall be donned by all involved personnel.

      - WORK PREPARATION

        - Protection of Existing Work to Remain:  Perform demolition work without damage or contamination of adjacent areas.  Where such work is damaged or contaminated, it shall be restored to its original condition.

        - Electrical:

          - All electrical work will be in conformance with the National Electrical Code.

          - Electrical Testing by Contractor:

            - The Contractor must notify the Owner, in writing, the name of the person performing the tests, date and time of tests and model number of equipment being used.

            - Prior to the installation of poly in any work area, testing of all electrical apparatus will be conducted by the Contractor.  Testing shall consist of the polarity of the circuits and a test to determine if any circuits are live in the project area.  All electrical equipment (i.e., motors, conduit, Greenfield, etc.) in the containment will be surface tested for ground

              - Extension Cords:  Extension cords utilized in the containment will be a minimum 12/2 wire with ground, neoprene or rubber covered.  Extension cords will be utilized in accordance with the National Electrical Code.

        - Work Areas:

          - The Asbestos/ Lead Foreman will establish designated limits for the asbestos/ lead control area.  With the use of rope for the asbestos/lead control area and barrier tape or other continuous barriers for the regulated area, maintain these and all other requirements for asbestos control areas.

          - Isolate the entire abatement area to anybody other than trained personnel and authorized visitors.  Erect signs around the perimeter in accordance with EPA, OSHA and this specification.  Maintain a log of all people entering and exiting the workplace.

          - Where designated on the drawings, separate parts of the building required to remain in use from parts of the building that will undergo asbestos abatement by means of airtight barriers constructed as follows:

            - Construct physical barrier as required by the asbestos/ lead designer.

            - Cover one side of the partition with a single layer of plastic sheet with joints staggered and sealed with tape.  Edges of partition at floor, walls and ceiling shall be caulked airtight.

          - Signs shall be posted at any location and approaches to a location where airborne concentrations of asbestos may exceed ambient background levels.  Signs shall be posted at a distance sufficiently far enough away from the work area to permit an employee to read the sign and take the necessary protective measures to avoid exposure.  Additional signs may need to be posted following construction of workplace enclosure barriers.  DO NOT ENTER signs will also be posted.

          - Shut down and lock out all heating, ventilating and air conditioning system (HVAC) components that are in, supply or pass through the work area.  (Note:  Interiors of existing ductwork may require decontamination.)  Double seal all intake and exhaust vents in the work area with successive layers of tape and 6-mil polyethylene.  Also seal any seams in system components that pass through the work area.  Remove all HVAC system filters and place in labeled 6-mil polyethylene bags for staging and eventual disposal as asbestos-contaminated waste.

          - Seal off all openings in the walls, ceiling and floor from inside the work area leading to outside areas by filling these openings with fiberglass then covering them with 6-mil polyethylene and duct tape.

          - When precleaning is not required, the Asbestos Air Monitor will inspect and approve each area prior to the sealing of all windows, doorways, elevator openings, corridor entrances, drains, ducts, grilles, grates, diffusers, skylights, and any other openings between the work area and uncontaminated area outside of the work area (including the outside of the building, tunnels and crawl spaces) (critical barrier) with new 6-mil polyethylene sheeting and tape.

          - Special attention is to be given the metal ducts, metal heater boxes and intake areas to ascertain that these are completely sealed with either polyethylene or some other means acceptable to the Engineer.

          - Preclean the work area by removing any loose, gross debris.

          - Preclean all fixed and movable objects in the work area using HEPA- filtered vacuums and/or wet cleaning techniques as appropriate.

            - Careful attention must be paid to machinery behind grilles or gratings where access may be difficult but contamination significant.

            - Also pay particular attention to wall, floor and ceiling penetrations behind fixed items.

            - After precleaning, enclose fixed objects in 4-mil polyethylene sheeting and seal securely in place with tape.

            - Where carpet is to remain and is scheduled on the drawings, such carpeting shall be thoroughly cleaned using HEPA vacuum equipment.

            - After precleaning, all furniture and equipment should be removed from the area if at all possible.

            - All electrical items and the communications systems shall receive special attention to avoid water/moisture damage.  All electrical equipment shall be completely covered with two (2) layers of plastic (6-mil minimum), each securely taped and sealed.  All telephones which cannot be removed to storage shall be wrapped in plastic bags.  In addition, these items shall be carefully monitored during the course of the work for penetration of the seal by water.  If water penetration is observed, reseal as required.

            - The Contractor is permitted one of two options with respect to lighting fixtures.  The fixtures may be removed by a licensed electrician or the fixtures may remain in place during construction provided that each is wrapped in polyethylene sheeting on the top surface and over all openings.  If fixtures are removed during construction, they shall be cleaned of all asbestos and dust, wrapped in polyethylene and stored in the designated storage area.

      - ISOLATION OF THE WORK AREA

        - Critical Barrier:

          - For all asbestos abatement projects which are performed in an occupied facility, large openings such as open doorways, elevator doors, and passageways shall be first sealed as a critical barrier.  The critical barrier shall constitute the outermost boundary of the asbestos abatement project work area.  Critical barriers shall be constructed in such a manner as to prevent unauthorized entry to the work area.  The work area shall be isolated by sealing all openings including, but not limited to, windows, doors, ventilation openings, drains, grilles, and grates with fiber-tight sheeting that is at least 6 mils thick (minimum) plastic sheeting and duct tape or the equivalent adhesive material to prevent the passage of asbestos fibers. All cracks, seams and openings in critical barriers shall be caulked or otherwise sealed, so as to prevent the movement of asbestos fibers out of the work area.  The adequacy of the containment design shall include consideration for special precautions to ensure the integrity of the critical barrier during all phases of the asbestos abatement project.

        - Establishing Containment Barriers:

          - Floor and wall surfaces shall be covered with fiber-tight sheeting.  All seams and joints shall be sealed with duct tape or equivalent adhesive material.  Floor covering shall consist of at least two layers of 6-mil thick fiber-tight sheeting and must cover at least the bottom 12 inches of the adjoining wall.  Wall covering shall consist of a minimum of two (2) layers of 4-mil thick fiber-tight sheeting which shall overlap the floor covering to prevent leaks.  There shall be no seams in the sheeting where the wall meets the floor.

Note:  Walls and ceilings that are non-porous and will not be damaged by water, surfactant, encapsulant do not necessarily need protection.  They can be decontaminated using HEPA vacuums and wet cleaning techniques.  Walls with mortar joints are considered porous, i.e., brick, concrete block, stone and glazed block tile.

          - Exceptions to the covering of floor, wall, and fixed object surfaces prior to starting an asbestos abatement project.

            - Where the glove-bag technique is to be used for the entire project, and a critical barrier has been established around the work area, and the work area can be maintained under negative pressure with a HEPA- filtered negative air machine.  In this instance, the critical barrier shall be considered a containment barrier for the purpose of compliance with Section 9(a)(4)(e) of the DEP Regulations.

            - Where non-porous and impervious material covers the floors, this material should be free from mortar joints, cracks, fissures, holes, or drain openings in which asbestos fibers may become trapped, lodged, or escape.

            - Where the physical dimensions of the work area are sufficiently small that the application of fiber-tight sheeting will likely result in disturbance of ACBM resulting in asbestos fiber release.  Such areas may include, but are not limited to, utility closets, crawl spaces, etc.

          - Acetate Windows 36" x 36" will be installed in a location or locations shown on the drawings.  Location of window or windows will be shown on the asbestos removal plan.  It is the intent that the work area be completely visible from the outside.

          - Emergency Breakthrough Points on the polyethylene will be clearly marked and always be accessible.  Arrows to emergency exits will be made on the polyethylene and be placed 2' off the floor.

          - Maintain emergency and fire exits from the work area, or establish alternative exits satisfactory to fire officials.

          - Physical Barrier will be a minimum of 3/8" plywood and heights as shown on the drawings, equipped with an emergency exit door of an approximate size of 3'-0" wide by 6'-3" high.  There shall be a surface mounted bolt-lock on the containment area side and the door shall swing out of the asbestos work area.  In the door will be a hinged opening with an acetate window.  A hasp, staple and padlock will be installed to maintain security in the door.

      - DECONTAMINATION FACILITIES

        - For each abatement area, provide decontamination facilities where shown on the drawings.  The decontamination facilities shall include a Personnel Decontamination Facility for workers and visitors and when designated on the drawings, a Waste Loadout System.

        - The Personnel Decontamination Facility shall consist of a three-room series as follows:  clean room, shower room, followed by a dirty/equipment room leading to the work area.

        - The clean room shall have sufficient space for storage of the worker's street clothes, towels, and other non-contaminated items.  Joint use of this space for other functions such as offices, storage of equipment, materials, or tools shall be prohibited.  Space heating or air conditioning will be in accordance with the drawings or conditions.

        - A shower room with two (2) curtained doorways.  Plastic on shower room and adjoining equipment and clean rooms shall be non-transparent.  Showers shall be provided and used at all asbestos removal operations.  Factory made shower head producing a spray of water which can be adjusted to spray size and intensity.  Feed shower with water mixed from hot and cold supply lines.  Arrange so that control of water temperature, flow rate, and shut off is from inside shower without outside aid.  Shower stall to have a soap dish.  The shower drain will be equipped with a 3 micron filter.

        - The shower room shall contain at least one (1) shower with hot and cold or warm water.  Careful attention shall be paid to the shower enclosure to ensure against leaking of any kind.  Ensure a supply of soap and disposable towels at all times in the shower room.  No electrical circuitry shall be located in the shower room.

        - When designated on the drawings, provide or construct a Waste Loadout System consisting of two (2) totally enclosed chambers as follows:

          - A bag wash area consisting of a water collection basin and/or collection and water filtration system, water hose and spray applicator.

          - A bagging area consisting of an airlock with a curtained doorway to the bag wash area and a curtained doorway to an uncontaminated area.

      - EQUIPMENT DECONTAMINATION

        - No equipment, supplies, or materials (except properly containerized waste material) shall be removed from an asbestos abatement project work area (including a containment barrier) unless such equipment, supplies and materials have been thoroughly decontaminated and cleaned free of visible debris.  Where the configuration of the equipment, supplies, materials to include cloth-canvas type shoes is such that decontamination is not feasible, the object shall be thoroughly wrapped in a minimum of two (2) layers of 6-mil fiber-tight sheeting with all joints, seams and overlaps sealed with tape; or containerized in a metal, plastic or fiber drum with a locking lid.

Examples include, but are not limited to, air filtration or HEPA vacuuming equipment, and wood or other materials used inside containment barrier to be transported to another containment barrier for reuse.  Equipment, supplies, or materials that have been wrapped for transport and storage shall be unwrapped only within a containment barrier under negative pressure.  For this purpose, the critical barrier shall be considered the containment barrier.

        - HEPA vacuums shall be emptied of collected asbestos waste prior to its removal from the containment barrier.  HEPA vacuums used as part of a glove bag removal shall be emptied within a containment barrier under negative pressure.  This containment barrier need not be at the work site.

        - Air filtration devices shall have used pre-filters removed, prior to removing the unit from the work area.  If the contaminated HEPA filter is not replaced after each job, the entire ventilation unit will be securely wrapped in 6-mil fiber-tight sheeting prior to removal from the work area.  Replace used filters within a containment barrier.  This facility need not be at the work site.

      - MAINTENANCE OF THE WORK AREA

        - Install portable exhaust ventilation system equipped with HEPA filters for the work area to maintain a minimum negative pressure of 0.02 inches of water.  If negative air pressure of 0.02 inches is lost, work shall be halted until negative air pressure is restored.  The exhaust ventilation system shall operate on a 24-hour basis throughout the abatement process and through the clearance air monitoring.  The exhaust ventilation system shall be designed in accordance with EPA recommendations included in the "Guidance for Controlling Friable Asbestos-Containing Materials in Buildings."  All exhaust ventilation units will be exhausted to the outside of the building.  Negative pressure will be provided inside the critical barrier from the time barrier construction has begun through the time that final clearance has been obtained.

        - Provide negative pressure recorder(s) to monitor the negative pressure differential.  The permanent record will be turned over to the Asbestos Air Monitor at the beginning of each workday and will become part of the Owner's documentation records.  If negative air pressure of 0.02" is lost, work shall be halted until negative air pressure is restored.

        - In a multi-room project, provide a sufficient number of portable exhaust ventilation units equipped with HEPA filters to create a flow of air from supply air openings toward the portable exhaust ventilation units to avoid any dead air pockets.

        - Make-up air entering the work area shall pass through the decontamination facility.  If an auxiliary air supply system is required, it will be located where shown on the drawings or in accordance with instructions from the Engineer.  The system will be filtered.  The filter will be mechanically fastened.  A plastic flap will be installed on the filter.

        - Acceptance of Containment Barrier Area:  Once the containment barrier has been constructed, the portable exhaust ventilation units put in place, the decontamination areas prepared, and the supplies to be used have been assembled, the Asbestos Air Monitor will notify the Engineer (in the event the Engineer is not in full time attendance) that the area is ready to inspect.  The Engineer and Asbestos Air Monitor may inspect the work area to ensure that barriers are properly constructed, that wall and ceiling openings are sealed, that 0.02 inches of water negative pressure has been achieved, and that all other preparations have been made to allow an efficient and safe removal operation to proceed.  If all conditions are found to be acceptable, the Engineer will allow the Contractor to proceed.  If conditions are not acceptable, the Contractor will correct the deficiencies.

      - ABATEMENT METHODS

        - Removal:

          - The asbestos will be removed in a wet state (See 40 CFR Part 61, Subpart M.  See 61.147).

          - Wet all asbestos-containing building material with an amended water solution using equipment capable of providing a fine spray mist in order to reduce airborne fiber concentrations when the material is disturbed.  Saturate the material to the substrate, however, do not allow excessive water to accumulate in the work area.  Keep all removed material wet enough to prevent fiber release until it can be containerized for disposal.  Maintain a high humidity in the work area by misting or spraying to assist in fiber settling and reduce airborne concentrations.  Wetting procedures are not equally effective on all types of asbestos-containing materials but shall nonetheless be used in all cases.

          - Saturated asbestos-containing building material shall be removed in manageable sections.  Removed material should be containerized before moving on to a new location for continuance of work.  Surrounding areas shall be periodically sprayed and maintained in a wet condition until visible material is cleaned up.

          - Material drop shall not exceed 10 feet.  For heights exceeding 10 feet, ACM must be containerized prior to lowering.

          - After completion of all stripping work, surfaces from which asbestos-containing materials have been removed shall be wet brushed and sponged or cleaned by some equivalent method to remove all visible residue.

          - During this work, the surfaces being cleaned shall be kept wet.

          - Containers (6-mil polyethylene bags or drums) shall be sealed when full.  Bags shall not be overfilled.  They shall be securely sealed to prevent accidental opening and leakage by tying tops of bags in an overhand knot or by taping in gooseneck fashion.  Do not seal bags with wire or cord.  Transport to wash room area of waste loadout.

          - Asbestos-containing waste with sharp-edged components which could tear the polyethylene bags or sheeting shall be place into burlap bags, then into poly bag and transported to wash room area of waste loadout.

          - Large components removed intact may be wrapped in one (1) layer of 6-mil polyethylene sheeting secured with tape for transport to the wash room area of the waste loadout.

          - Bags shall be washed and transferred to the bagging room for double bagging.

          - Large components shall be washed and transferred to the bagging room to be double wrapped.

          - A coating or encapsulating agent shall be applied to any porous surface that has been stripped and thoroughly cleaned of asbestos-containing materials.  The encapsulating agent should also provide a surface that can accommodate subsequent coverings after the project is complete.

        - Special Circumstances:

          - In some instances, the suspended ceiling and/or the plaster ceiling must be demolished or partially demolished in order to repair plaster, encapsulate asbestos, or remove asbestos.  Portions of these ceilings may be contaminated with asbestos debris.  In general, in locations where asbestos removal will ultimately take place, the ceilings shall be demolished under asbestos removal conditions and the debris disposed of as asbestos debris.  The Contractor should note that there could be some exceptions to this general rule as determined by the Engineer and the Asbestos Air Monitor.

          - Inspection During Removal:  While performing asbestos removal work, the Contractor may be subject to periodic inspections and constant observation by the Asbestos Air Monitor and/or the Engineer who may be assisted by other safety or health personnel.  If at any time the asbestos removal work is found to be in violation of this specification, the Engineer or the Asbestos Air Monitor will issue a stop work order to be in effect immediately and until the violation is resolved.

          - Standby time required to resolve the violation shall be at the Contractor's expense.  Also, if the fiber count inside the containment area goes over .5 fibers/cc or the negative pressure in the containment area drops below 0.02 inches of water, the job will shut down and corrective actions taken prior to continuing.  Shutdown will also occur if airborne fiber concentrations are found to be in excess of 0.01 f/cc in the clean room and any outside areas, a break occurs in the barrier, failure of workers to wear respiratory protection, or poor housekeeping inside or outside the contained area.

        - Glove Bag Removal:

          - Glove bags may be used for the removal of a short length of pipe lagging with outside diameters less than 5".  Glove bags shall require the construction of a critical barrier.  A portable exhaust ventilating unit will operate in the containment.  Maintaining .02" of negative pressure.  Asbestos from larger diameter pipes will be removed in a containment barrier as described elsewhere in this specification.

          - Personal Safety:  The glove bag asbestos removal method must be done properly using all equipment and materials specified, thus there should be no fibers released into the ambient air.  However, it is possible that an accident could occur (such as tearing of the bag) that would release fibers in the vicinity of the workers.  Also, improper seals during preparation would result in the same condition.  Therefore, the workers are required to use the following personal protective equipment:

            - Dual Cartridge Respirator:  A dual cartridge respirator shall be used and selected from among those approved by the NIOSH, Dept. of Health and Human Services, under the provisions of 30 CFR Part II (37 F.R. 6244, March 25, 1972).  The filters shall be rated for asbestos-containing dusts.  Any asbestos-rated powered air purifying or type "C" supplied air respirator may be used to offer an increased protection factor.

            - Disposable Clothing:  Disposable clothing, including coveralls, hoods, and booties shall be worn during the "glove bag" process from preparation of the pipe through final inspection.  When the used glove bag has been placed in the 6-mil disposal bag, the disposable clothing should also be placed in the bag, sealed with tape or a tie, and stored in the sealed barrel until it can be taken to the landfill.  Filters from air purifying respirators must also be disposed of as asbestos-contaminated debris.

            - Showers:  Showers are not necessarily required by workers after each "glove bag" removal.  However, before each project, a portable shower shall be set up and available near the work area.

            - Each worker may take a shower after completing an uninterrupted sequence of removal if he/she so desires, using soap and warm water whether known contamination has taken place or not.  Each worker will wash face and hands after removal work and before smoke breaks, lunch, end of the workday or any other break in work.  If the project requires the use of more than one glove bag, a shower must be taken.

            - Background, area and final clearance air monitoring will be required during the removal process.  Glove bag removal is not to begin until approval has been obtained from the Asbestos Air Monitor.  An inspection will also be conducted prior to initiating a glove bag removal to ensure that a layer of plastic has been placed under the work area and all porous wall surfaces are covered and that a portable exhaust ventilation unit equipped with HEPA filters is in operation.  This inspection will also determine that the glove bag has been properly attached to the pipe and that all necessary tools are available.

          - Removal:  The following steps, if done with care and attention to detail, will isolate sections of piping, valves, fittings, pipe knuckles, etc., to allow asbestos-containing insulation or lagging to be removed without allowing fibers to become airborne outside the bag.  Two workmen are required for each glove bag removal.

            - Isolate the area in which removal will take place by placing barrier tape at least 6 feet external from all open entrances to affected room.  Lock from external entry all but one entrance whenever possible.  Determine emergency exit provisions, ideally inside panic bar fitted doors, otherwise, have key available.  A wider area may be blocked off with barrier tape at the discretion of the Asbestos Air Monitor.

            - Place asbestos warning signs at all open entrances to work area conspicuously and so they can be easily read.  They must conform to legal size and wording as specified in 29 CFR 1919.1001 and 1926.1101.

            - Turn off or isolate HVAC system in work area from the rest of the building.  Contact Engineer to inspect before proceeding with work; or in the event this is not possible, the Engineer will detail appropriate emergency provisions to turn off system.

            - Construct a critical barrier and establish negative air.

            - Put on fitted respirators and disposable coveralls, hood and booties.  Ensure that disposable clothing is sealed with duct tape at wrists, ankles and neck area.  This procedure is for a single glove bag.  For multiple glove bag operations. full decontamination procedures are to be followed.

            - Double-check pipe, valve, etc., to ensure it is not too hot to work on.  It is preferable that all services be shut down to work site for worker's safety.

            - Check HEPA vacuum to prevent circuit overload from hampering work in progress.  If circuit blows, do not proceed until line with sufficient power is secured..

        - ROOFING REMOVAL

          - Everyone inside the regulated area must have full worker protection.  The area will be de-regulated at daily abatement completion, then re-regulated the following day of abatement.

          - Remove all asbestos patching, felts and flashings to include felts under gravel stop where shown on the drawings.

          - During the removal process, the asbestos-containing felts and flashings will be kept moist.  Any debris will be picked up by a HEPA vacuum or other means approved by the Engineer.  Discharge no visible emission during collection, packaging, transporting, or deposition.  Felts are to be removed down to the insulation or to non-asbestos-containing material.

          - Cut felts and flashing in manageable pieces.  Cutting method to be approved by the Engineer.  Collect felts, etc., and place in burlap bags which will be inside double 6-mil poly bags.  Collect other asbestos waste, scrap, debris, and asbestos-contaminated clothing and seal in double 6-mil impermeable poly bags.  Affix a caution label to each bag and dispose of in accordance with these specifications.

          - Any mastic residue in a non-friable condition on metal, masonry, etc., that cannot be removed without damage to the substrate may remain.

          - All roofing abatement equipment to be cleaned, secured, and inspected by an Independent Asbestos Inspector before the abatement crew leaves the project, and or before the roof is covered with the new roof system.

        - Encapsulation: No abated pipes will be “encapsulated” and or “Lockdown” prior to visual inspection and air clearances.

        - Asbestos Enclosure:

          - Enclosing asbestos-containing material behind a rigid fiber-tight barrier without disturbing asbestos or causing a fiber release episode will be accomplished in the following manner:

            - The workplace enclosure requirements stated in the Department of Environmental Protection Rules and Regulations shall apply when enclosing asbestos-containing material behind a rigid fiber-tight barrier.

            - All areas of asbestos-containing materials shall be sprayed with water if those areas may be disturbed during the installation of hangers, brackets or other portions of the fiber-tight barrier.

            - All loose and hanging asbestos-containing material shall be removed as follows:

            - All asbestos-containing material shall be adequately wetted using a water solution or equivalent wetting agent throughout the removal process until disposal.

            - If structural components are to be removed, they shall be wrapped and removed intact or in large sections whenever possible and carefully lowered to the floor.  Structural components shall be thoroughly wetted prior to wrapping in fiber-tight sheeting for disposal.  Water shall be visible or evident inside the wrapping.

            - Asbestos-containing material shall not be dropped or thrown to the floor level.  Asbestos-containing material may be carefully lowered to a raised scaffolding or containerized at elevated levels for transport and disposal.

            - A coating or encapsulating agent shall be applied to any porous surface that has been stripped of asbestos-containing materials to securely seal any residual fibers that may be present.  The encapsulating agent should be chosen so as not to damage or weaken the substrate on which it is to be applied and should adequately adhere to the substrate.  The encapsulating agent should also provide a surface that can accommodate subsequent coverings after the project is complete.

          - Non-asbestos-containing substitutes shall be used to patch thermal insulation and fireproofing materials when required and where appropriate.

          - Enclosures for asbestos-containing materials shall be specifically designated by signs, labels, color coding, or some mechanism to warn individuals who may be required to disturb or enter the enclosure.

          - Clean up shall be in accordance with the following section on "Final Clean Up and Inspection Procedure."

        - Specific Requirements - Encapsulation - Glove Bag:  Prior to removal of the glove bag, a spray- type encapsulant will be used to seal the friable ends.  Application to be in strict accordance with the manufacturer's recommendations.

      - FINAL CLEANUP AND INSPECTION PROCEDURE

        - After the removal, encapsulation, and/or enclosure of asbestos has been completed and before removal of barriers, piping and all other surfaces within the work area shall be thoroughly wet cleaned and/or vacuumed.  Waste containers (except those containers necessary for waste from final cleanup) shall be packed, cleaned, and removed from the work area prior to final cleanup and monitoring.

        - The specific instructions for cleaning and clearance will be found in Section 01014AA - Work Sequence and Special Instructions – Interior, and or Section 01015AA - Work Sequence and Special Instructions – Roofs, The work area must be clean and in accordance with ASTM E 1368-90.

        - Clearance air monitoring will be conducted in accordance with the protocol established in Division 1 - General Requirements, Section 01410AA - Testing Laboratory Services - Asbestos.

        - Responsibility for Damages:  Any damage to the finishes, floor, walls, or any other items or fixtures that has been the result of actions by the Contractor's personnel shall be repaired to their original condition without any additional cost to the Owner.

      - REINSTALLATION OF EQUIPMENT

        - When cleanup is complete, relocate objects moved to temporary locations in the course of the work to their proper positions.

      - DISPOSAL

        - Collect asbestos waste, scrap, debris, bags, containers, equipment, and asbestos-contaminated clothing which may produce airborne concentrations of asbestos fibers thoroughly wetted and seal in double 6-mil impermeable poly bags.  Affix a caution label to each bag.  For temporary storage, store sealed impermeable bags in asbestos waste drums or skips.  An area for interim storage of asbestos waste-containing drums or skips will be assigned by the Engineer.  The asbestos-containing building material may be placed in a locked truck and kept on location until the truck is fully loaded.  When the asbestos-containing building material is ready to be hauled to the landfill, arrangements will be made for an escort if one is required.  The asbestos-containing building material will be moved to the landfill in full loads during the daytime.

        - Procedure for hauling and disposal shall comply with 40 CFR 61 (Subpart B), state, regional, and local standards.  Dispose of waste asbestos material at an Environmental Protection Agency (EPA) or state-approved sanitary landfill.  Sealed plastic bags may be dumped from drums into the burial site unless the bags have been broken or damaged.  Damaged bags shall remain in the drum and the entire contaminated drum shall be buried.  Uncontaminated drums may be recycled.  Workers unloading the sealed drums shall wear appropriate respirators and personal protective equipment when handling asbestos materials at the disposal site.

        - Receipts will be furnished to driver and be completed in full at the landfill showing date, time received, vehicle license number, signature of landfill receiver and cubic volume of material.  Receipts to be forwarded to Engineer as required in Section 01300AA - Submittals - Asbestos.

        - The Asbestos Foreman will visually inspect the interior of the truck body for cleanliness before loading begins.  If the truck body has any visible residue of asbestos, the body is to be thoroughly cleaned before using.

END OF SECTION 13280