28 April 2005

Mr. David Fenstermacher, P.E.,

Vanasse Hangen Brustlin, Incorporated,

Post Office Box: 9151,

Watertown, Massachusetts 02472

RE:  The Capacity to Handle the Anticipated Wastewater Flows, From “Morrill’s crossing,”

33 Allen Avenue, A Proposed Retail, Residential, Boxing Club Project.

Dear Mr. Fenstermacher:

The existing eight-inch diameter asbestos concrete sanitary sewer pipe, located in Cambridge Street, has adequate capacity to transport, while The Portland Water District sewage treatment facilities, located off Marginal Way, have adequate capacity to treat the anticipated wastewater flows of 22,948 G.P.D., from the proposed retail, residential, boxing club project.

Anticipated Wastewater Flows from the Proposed Project:

1 Proposed 65,821 S.F. “Shop & Shop,” Supermarket @ 0.1 G.P.D/S.F. =   6,582 G.P.D.

6 Proposed 62,300 S.F. Miscellaneous Retail Units @ 0.1 G.P.D/S.F.	  =   6,230 G.P.D.

30 Proposed Two Bedroom Units, @ 180 G.P.D/Unit			  =   5,400 G.P.D.

1200 Proposed Boxing Club Spectators @ 3 G.P.D/Spectator		  =   3,600 G.P.D.

50 Proposed Boxing Club Participants, @ 10 G.P.D/Participant		  =      500 G.P.D.

5 Proposed Boxing Club Employees, @ 15 G.P.D/Employee		  =        75 G.P.D.

561 Proposed Parking Spaces @ 1 G.P.D/Space				  =      561 G.P.D.

Total Proposed Increase in Wastewater Flows for this Project		  = 22,948 G.P.D.

The City combined sewer overflow (C.S.O.) abatement consent agreement, with the U.S.E.P.A. and with the Maine D.E.P., requires C.S.O. abatement, as well as storm water mitigation, from all projects, in order to offset any increase in sanitary flows.

If The City can be of further assistance, please call 874-8832.

Sincerely,

CITY OF PORTLAND

Frank J Brancely, B.A., and M.A.

Senior Engineering Technician

FJB

cc:	Alexander Q. Jaegerman, Director, Department of Planning, and Urban Development, City of Portland

Sarah Hopkins, Senior Development Review Manager, Department of Planning, and Urban Development, City of Portland

Eric Labelle, P.E., City Engineer, City of Portland

Bradley A. Roland, P.E., Environmental Projects Engineer, City of Portland

Stephen K. Harris, Assistant Engineer, City of Portland

Jane Ward, Administrative Assistant, City of Portland

Desk file