March 31, 2009

Memo To:	Eric Giles

From: 		David Margolis-Pineo and Staff at Public Services

Re:		Morrill’s Crossing Review Comments

It is realized that this project has already received Planning Board approval.  The following comments are offered for the applicant’s benefit when construction has begun.  If the applicant has any questions, they may contact me at 874-8850 or Todd Merkle at 874-8833.

- Please note that the grease trap detail does not meet City standards.  Please contact Steve Harris at 874-8843.

- Capacity letter completed 4/29/05.  Have conditions changed to require a revised capacity letter?

- There should be 10" of gravel on sheet C-11 if sidewalk is in the City ROW.

- Concrete is not allowed in the City ROW to backfill curbing.

- 3' sumps are the City standard in catch basins, not 4'.  But 4’ is permitted.

- City standard is 6" of 3/4" crushed stone under all structures.

- Catch basin frames and covers to be Ethridge E24" x 5” or approved equal is the City standard.

- Pipe boots are required in all catchbasins pipe connections.

- Inverts in DMH's are to be brick with concrete or masonry fill

- All pipes in the City right of way to be SDR 35 or RCP pipe, no HDPE is allowed.

- The City standard for pipe installation is 6"under and 12" over of 3/4" crushed stone.

- All storm drain manhole covers to be stamped DRAIN and all sanitary sewer manhole covers to be stamped SEWER.

- No inside drops are allowed in a sanitary sewer manhole in the City ROW.

- All joints between sections of precast concrete structures to be double sealed with Butyl rubber.

- Curb installation to be per City standard.

- All work in the City ROW shall adhere to the Street Opening Rules and Regulations and preformed by a licensed excavator with the City of Portland.

- The work in Allen Ave and Forest Ave is restricted to between 9 AM and 3:30 PM. A time waiver may be requested to work outside those hours from Public Services.